## G. SUM
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
GRAND SUMMARY
BILL NO. | DESCRIPTION | AMOUNT
Rs. Cts.
1 | PRELIMINARIES | 81569500
2 | BUILDING WORKS | 1385387911.662
3 | ATTENDENCE FEE AND BUILDR'S WORK FOR NOMINATED SUB CONTRACTOR'S WORK | 32560000
| SUB TOTAL (1) | 1499517411.662
| Less - Provisional Sum (Excluding Money Provision for Nominated sub contractor's work) | -43734500
| SUB TOTAL (2) | 1455782911.662
DISCOUNT IF ANY (………..%)
| SUB TOTAL AFTER DISCOUNT (3) | 1455782911.662
| Add - Provisional Sum, above mentioned | 43734500
| BID PRICE (WITHOUT VAT) CARRIED TO FORM OF BID | 1499517411.662
Tender Amount (in words) Rupees : One Billion Four Hundred Ninety Nine million Five Hundred Seventeen Thousand Four Hundred Eleven and Cents Sixty Six Only
Name of Tenderer : ……………………......................…………….……..………...……
Address : ……………...…......................................…………...…………
Tenderer's VAT No. (if any) ……………………………….....................................
Signature and Seal :

## mode-pay
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
BILL OF QUANTITIES
Mode of Payment | Item Nr
Reimbursement of actual cost on submission of the relevant documents acceptable to the Engineer plus 5% of the actual cost of obtaining the Insurance Policies and Securities. | B1/01, B1/02, B1/03, B1/04,
To be paid on signing of the formal Contract Agreement. | B
60% on completion of temporary buildings or structures. 30% in equal installments over the contract period and balance 10% on dismantling and removal on completion. | B2/01, B3/01, B3/02, B3/03,
Paid on satisfactorily completion of the item. | B2/02, B3/04, B6/04
In equal installments over the contract period. | B2/03, B3/05, B4/01, B4/02, B6/01, B6/02, B6/03, B7/01, B7/02, B8/01, B8/02
Mode of payment to be mutually agreed between Contractor and the Employer at the commencement of contract in relation to the programme of work. | B5/01, B9/01
On the completion of Works. | B7/03

## prelem
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
BILL NO. - 1 |  | PRELIMINARIES
Item No | Description | Mode of Payment Category | Unit | Amount
B/- | PRELIMINARIES
B1 | Insurance and Securities
B1/01 | Provisional sum for providing a Performance Security. | A | PS | 832000
B1/02 | Provisional sum for providing an Advance Payment Security. | A | PS | 3330000
B1/03 | Provisional sum for insurance of Works, Machinery & Equipment, Plant, Materials, third party persons & property and Employer's personnel & property at site as per the Contract. | A | PS | 6105000
B1/04 | Provisional sum for insurance against accidents and injury to Contractor's personnel as per the Contract. | A | PS | 277500
B2 | Engineer's Facilities
B2/01 | Allow lump sum for constructing, maintaining, dismantling and removal on completion of the Works, a temporary building for Engineer's office, including necessary furniture and fittings, furnishing, sanitary facilities, etc. | C | Item | Existing facilities shall use
B2/02 | Allow lump sum for providing telephone, facsimile facilities, electricity and water services for the Engineer's site office for their use in connection with the Works. | D | Item | Existing facilities shall use
B2/03 | Allow lump sum for maintenance, rental, consumption charges etc. for telephone and facsimile facilities, electricity and water services for the Engineer's site office for their use in connection with the Works. | E | Item | Existing facilities shall use
B3 | Contractor's Facilities
B3/01 | Allow lump sum for constructing, maintaining, dismantling and removal on completion of the Works, a temporary site office including staff rest room and toilets and other facilities for the Contractor's site management office. | C | Item | 550000
B3/02 | Allow lump sum for constructing, maintaining, dismantling and removal on completion of the Works, building to be used as workshops and stores for perishable materials. | C | Item | 400000
B3/03 | Allow lump sum for constructing, maintaining, dismantling and removal on completion of the Works, temporary buildings to accommodate the following; | C | Item | 1825000
1. Workers' rest room, kitchen
2. Toilet and wash areas
3. Sick/First-Aid room
4. Accommodation for Contractor's staff and workmen including sanitary facilities on site
B3/04 | Allow lump sum for providing telephone and facsimile facilities, electricity and water services for the Contractor's site office for their use in connection with the Works. | D | Item | 150000
B3/05 | Allow lump sum for maintenance, rental, consumption charges, etc. for telephone and facsimile facilities, electricity and water services for the Contractor's site office for their use in connection with the Works. | E | Item | 1100000
B4 | Construction Management and Supervision
B4/01 | Allow lump sum for employing suitably qualified and experienced technical personnel on full time basis for Construction Management Services at the site. | E | Item | 18000000
B4/02 | Allow lump sum for employing technical supervisory staff on full time basis. | E | Item | 17500000
B5 | Setting Out
B5/01 | Allow lump sum for setting out of Works in accordance with drawings and other written information given by the Engineer. | F | Item | 1500000
B6 | Quality, Standards and Progress
B6/01 | Allow lump sum for provision of progress reports including photographic records and other schedules included in the ICTAD publication - Guidelines for Effective Construction Management (ICTAD/CM/01). | E | Item | 220000
B6/02 | Allow lump sum for all cost in connection with preparing samples for testing, making arrangements for testing of materials, Goods, etc., as stipulated in the specification, obtaining test reports and submitting to the Engineer. | E | Item | 630000
B6/03 | Allow lump sum for provision of shop drawings, bar schedules, etc. for Engineer's approval. | E | Item | 260000
B6/04 | Allow lump sum for provision of two sets of (hard copies and soft copies) as-built drawings of all services, (except nominated sub contractor's work) for Engineer's approval. | D | Item | 200000
B7 | Health, Safety and Environment
B7/01 | Allow lump sum for providing all necessary safety measures to workmen at site conforming to the latest industrial safety regulations and as directed by the Engineer. Safety visibility vests, rain-jackets, helmets and safety footwear shall be essential safety items. | E | Item | 6350000
B7/02 | Allow lump sum for making adequate provisions against air and noise pollution of surrounding areas. Hoarding and dust screens shall be provided to control dust escaping to surrounding areas. | E | Item | 450000
B7/03 | Allow lump sum for demobilization, removal of all rubbish & debris and clearing up site on completion, leaving all in good order and handing over. | G | Item | 640000
B8 | Security and Protection
B8/01 | Allow lump sum for employing an adequate number of security personnel and security systems on full time basis throughout the period of construction, and provide all necessary security lighting and a warning system. | E | Item | 3000000
B8/02 | Allow lump sum for providing and maintaining necessary fencing, hoarding and gates for safeguarding the Works, Materials and Plant, as directed by the Engineer. | E | Item | 1500000
B9 | Miscellaneous
B9/01 | Allow lump sum for providing any other item related to preliminary work during construction period. The constractor shall mention such items. |  | Item | 16750000
| B - Preliminaries |  |  | 81569500
Total Carried to Summary

## SUMMARY
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
SUMMARY - BILL NO. - 2 - BUILDING WORKS
ITEM | DESCRIPTION | AMOUNT
D | EXCAVATION AND EARTH WORK | 6450101
F | CONCRETE WORK | 627880545.816
G | MASONRY WORK | 65734512
H | WATER PROOFING | 51369263
K | METAL WORK | 138018049
P | ROOF COVERING | 5578933
Q | WATER SUPPLY | By Nominated Sub Contractor
S | ELECTRICAL | 172924342
T | FLOOR/WALL/CEILING FINISHES | 267292814.846
V | PAINTING | 34677025
W | SOIL & WASTE WATER SYSTEM | By Nominated Sub Contractor
Y | MISCELLANEOUS | 15462326
| TOTAL CARRIED TO GRAND SUMMARY | 1385387911.662

## E.wk
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
BILL OF QUANTITIES |  | EXCAVATION AND EARTHWORK
ITEM NO | DESCRIPTION | UNIT | Qty | RATE (RS) | AMOUNT (RS)
D/- | EXCAVATION AND EARTHWORK
Site Clearing
| Reduced level excavation is already done | Note
| The Bidder is required to visit the site of the proposed work before pricing the following items. | Note
| Refer Pricing Preambles, Soil Investigation Report and Excavation and Earth work secion of the Specification before pricing the following items. | Note
| Unless other wise stated, Rate shall include for: | Note
| Back filling with selected excavated material & consolidating, surface treatment, compaction before filling / foundation. | Note
D/1 | Excavation for foundation in any materials met with except rock requiring blasting, depth not exceeding 2.0m from the reduce level. Part return fill in ram & surplus disposed of within site as directed.
D/1 | Lower Ground floor
D/1/1 | In Column footing | m3 | 156 | 1536 | 239616
0
D/1/2 | in pile cap | m3 | 84 | 1233 | 103572
0
D/1/3 | in ground beam & shear wall | m3 | 93 | 1233 | 114669
0
D/1/4 | in lift well | m3 | 84 | 1233 | 103572
0
D/1/5 | Stair case footing | m3 | 4 | 1233 | 4932
D/2 | Excavation for pit in any materials met with except rock requiring blasting, depth not exceeding 3.5m from the reduce level. Part return fill in ram & surplus disposed of within site as directed.
D/2/1 | Pit for water sump | m3 | 512 | 1258 | 644096
0
D/3 | Uper Ground floor |  |  |  | 0
D/3/1 | In Column footing | m3 | 84 | 1567 | 131628
0
D/3/2 | in pile cap | m3 | 34 | 1258 | 42772
0
D/3/3 | in ground beam | m3 | 114 | 1258 | 143412
0
D/3/4 | Stair case footing | m3 | 4 | 1258 | 5032
D/4 | Rock excavation requiring blasting, depth not exceeding 3.5m from the reduce level and disposed of within site as directed. (Provisional quantity) | m3 | 100 | 16380 | 1638000
0
D/5 | Filling with excavated soil availabe at site in the area below the ground floor slab to achieve 95% Procted density.
D/5/1 | In lower Ground floor | m3 | 988 | 1010 | 997880
0
D/5/2 | In Ground floor | m3 | 492 | 1010 | 496920
D/6 | Termite proof physical barrier that contains termite Proof Cementitious parge / Resin applied at DPC level to approved specialist contractor's specifications. Contractor shall provide 15 year warranty for whole treatment
D/6/1 | In lower Ground floor (Provisional Qty. ) | m | 1000 | 692 | 692000
D/6/2 | In Ground floor (Provisional Qty. ) | m | 1000 | 692 | 692000
D/07 | Allow sum for dewatering relevant to substructure construction (if necessary) Contractor shall submit relevant quotation and approval should be obtained before commencing the work. | Item | Allow | P.Sum | 200000
D/08 | Allow sum for shoring ,suitable for the ground condition. Contractor shall submit relevant quotation and approval should be obtained before commencing the work. | Item | Allow | P.Sum | 200000
| TOTAL CARRIED TO SUMMARY |  |  | RS. | 6450101

## Concrete
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
BILL OF QUANTITIES |  | CONCRETE WORKS
ITEM NO | DESCRIPTION | UNIT | QTY. | RATE (RS) | AMOUNT (RS)
F | CONCRETE WORKS
Concrete ,Grade 15, 1:3:6 (40)
F/1 | 50mm thick lean concrete under:
| Lower ground floor | [5 empty] | 309395500.816
F/1/1 | In pile cap | m2 | 117 | 645 | 75465
0
F/1/2 | In column footing (F1, F2, F3, F4,) | m2 | 104 | 645 | 67080
0
F/1/3 | In ground beam & shear wall | m2 | 312 | 645 | 201240
0
F/1/4 | In lift well | m2 | 56 | 645 | 36120
0
F/1/5 | In Stair footing | m2 | 6 | 645 | 3870
0
F/1/6 | Water sump Base slab | m2 | 187 | 645 | 120615 | Addendum 02
0
| Ground floor |  |  | 0
F/1/7 | In pile cap | m2 | 48 | 645 | 30960
0
F/1/8 | In column footing (F3, F4,) | m2 | 56 | 645 | 36120
0
F/1/9 | In ground beam | m2 | 226 | 645 | 145770
0
F/1/10 | In Stair footing | m2 | 2 | 645 | 1290
0
F/2 | Concrete filling to form required level (Gr.15 concrete to 50mm avarage thick) in toilet area |  |  | 0
F/2/1 | At G/F level | m2 | 1 | 645 | 645
F/2/2 | At 1st F/ level | m2 | 32 | 665 | 21280
F/2/3 | At 2nd F/ level | m2 | 28 | 686 | 19208
F/2/4 | At 3rd F/ level | m2 | 34 | 707 | 24038
F/2/5 | At 4th F/ level | m2 | 19 | 728 | 13832
F/2/6 | At 5th F/ level | m2 | 14 | 751 | 10514
F/2/7 | At 6th F/ level | m2 | 12 | 774 | 9288
F/2/8 | At 7th F/ level | m2 | 12 | 798 | 9576
F/2/9 | At 8th F/ level | m2 | 20 | 822 | 16440
0
F/3 | Concrete Grade 25 (Ready mixed where necessary) in the following |  |  | 0
| Lower ground floor |  |  | 0
F/3/1 | In pile cap | m3 | 183 | 19392 | 3548736
0
F/3/2 | In column footing (F1, F2, F3, F4,) | m3 | 42 | 19392 | 814464
0
F/3/3 | In ground beam & sheer wall footing (between pile cap column and under Retain wall) | m3 | 192 | 19392 | 3723264
0
F/3/4 | In retaining wall up to G/F level | m3 | 206 | 19392 | 3994752
0
F/3/5 | In Bottum slab of Lift well | m3 | 25 | 19392 | 484800
0
F/3/6 | In walls at lift well up to Lower G/F level | m3 | 19 | 19392 | 368448
0
F/3/7 | In Column (300x300mm,single story building) | m3 | 2 | 19392 | 38784
0
F/3/8 | In Column (600x600 mm ) | m3 | 25 | 19392 | 484800
0
F/3/9 | In Stair footing & wall up to Lower G/F level | m3 | 4 | 19392 | 77568
0
F/4 | Concrete Grade 35 (Ready mixed where necessary) in the following |  |  | 0
| Water sump @ Lower ground floor |  |  | 0
| Refer Dwg No: HB/ST/24/T |  |  | 0
F/4/1 | Base slab, 350mm thick | m3 | 66 | 21003 | 1386198
0
F/4/2 | Wall, 250mm thick | m3 | 40 | 21003 | 840120
0
F/4/3 | Top slab, 150mm thick including kerb at opening | m3 | 26 | 21003 | 546078
0
F/4/4 | Top slab beam , 300x650mm | m3 | 5 | 21003 | 105015
0
F/4/5 | Refer Miscellaneous work for other ancillary items in water sump | Note |  | 0
0
| Ground floor |  |  | 0
F/4/6 | In pile cap | m3 | 54 | 21003 | 1134162
0
F/4/7 | In column footing | m3 | 117 | 21003 | 2457351
0
F/4/8 | In ground beam (between pile cap and column) | m3 | 178 | 21003 | 3738534
0
F/4/9 | In Column (300x300mm,single story building) | m3 | 7 | 21003 | 147021
0
F/4/10 | In Column (450x450mm ) | m3 | 6 | 21003 | 126018
0
F/4/11 | In Column (600x600 mm ) | m3 | 24 | 21003 | 504072
0
F/4/12 | In Stair footing & wall up to G/F level | m3 | 3 | 21003 | 63009
0
F/5 | Concrete Grade 20 (Ready mixed where necessary) in the following |  |  | 0
0
F/5/1 | Ground floor slab of Lower G/F (thickness 100mm) and incresing of thickness by 150mm where walls exit above slab and free edges as shown in detail, Rate shall include for Reinforcement net, 10mm bars at 250mm, both ways | m3 | 174 | 28732 | 4999368
0
F/5/2 | - dito - but for Ground floor slab (include porch area) | m3 | 152 | 28732 | 4367264
F/6 | Precast Concrete
F/6 | Casting, handling and placing Precast Concrete slab as shown in the Dwg. No: HB/DT/22-T
Rate shall include all expenses for mesh ( Bottom) & bar reinforcement (trangulated lattice girder), Casting at yard (including preparation and maintenance of yard), curing, handling, and placing
F/6/1 | At G/F level
Precast concrete slab
F/6/1/1 | Size, 5100x1200x60mm | Nr. | 278 | 41774.4 | 11613283.2
F/6/1/2 | Size, 5100x1100x60mm | Nr. | 3 | 40557.552 | 121672.656
F/6/1/2 | Size, 5100x1000x60mm | Nr. | 4 | 39351.648 | 157406.592
F/6/1/3 | Size, 5000x800x60mm | Nr. | 11 | 35554.272 | 391096.992
F/6/1/4 | Size, 5000x600x60mm | Nr. | 2 | 32107.728 | 64215.456
F/6/1/5 | Size, 5000x500 or 400x60mm | Nr. | 2 | 30702.96 | 61405.92
F/6/2 | At 1st/F level
Precast concrete slab
F/6/2/1 | Size, 5100x1200x60mm | Nr. | 472 | 42193 | 19915096
F/6/2/2 | Size, 5100x1100x60mm | Nr. |  | 40964 | 0
F/6/2/3 | Size, 5100x1000x60mm | Nr. | 1 | 39746 | 39746
F/6/2/4 | Size, 5000x800x60mm | Nr. | 17 | 35910 | 610470
F/6/2/5 | Size, 5000x600x60mm | Nr. | 7 | 32429 | 227003
F/6/2/6 | Size, 5000x500 or 400x60mm | Nr. | 2 | 31010 | 62020
F/6/3 | At 2nd/F level
Precast concrete slab
F/6/3/1 | Size, 5100x1200x60mm | Nr. | 397 | 42615 | 16918155
F/6/3/2 | Size, 5100x1100x60mm | Nr. | 2 | 41374 | 82748
F/6/3/3 | Size, 5100x1000x60mm | Nr. | 1 | 40144 | 40144
F/6/3/4 | Size, 5000x800x60mm | Nr. | 13 | 36270 | 471510
F/6/3/5 | Size, 5000x600x60mm | Nr. | 1 | 32754 | 32754
F/6/3/6 | Size, 5000x500 or 400x60mm | Nr. | 1 | 31321 | 31321
F/6/4 | At 3rd/F level
Precast concrete slab
F/6/4/1 | Size, 5100x1200x60mm | Nr. | 248 | 43042 | 10674416
F/6/4/2 | Size, 5100x1100x60mm | Nr. | 2 | 41788 | 83576
F/6/4/3 | Size, 5100x1000x60mm | Nr. | 1 | 40546 | 40546
F/6/4/4 | Size, 5000x800x60mm | Nr. | 10 | 36633 | 366330
F/6/4/5 | Size, 5000x600x60mm | Nr. | 2 | 33082 | 66164
F/6/4/6 | Size, 5000x500 or 400x60mm | Nr. | 2 | 31635 | 63270
F/6/5 | At 4th/F level
Precast concrete slab
F/6/5/1 | Size, 5100x1200x60mm | Nr. | 261 | 43473 | 11346453
F/6/5/2 | Size, 5100x1100x60mm | Nr. | 1 | 42206 | 42206
F/6/5/3 | Size, 5100x1000x60mm | Nr. | 1 | 40952 | 40952
F/6/5/4 | Size, 5000x800x60mm | Nr. | 11 | 37000 | 407000
F/6/5/5 | Size, 5000x600x60mm | Nr. | 4 | 33413 | 133652
F/6/5/6 | Size, 5000x500 or 400x60mm | Nr. | 2 | 31952 | 63904
F/6/6 | At 5th/F level
Precast concrete slab
F/6/6/1 | Size, 5100x1200x60mm | Nr. | 261 | 43865 | 11448765
F/6/6/2 | Size, 5100x1100x60mm | Nr. | 1 | 42629 | 42629
F/6/6/3 | Size, 5100x1000x60mm | Nr. | 1 | 41362 | 41362
F/6/6/4 | Size, 5000x800x60mm | Nr. | 11 | 37370 | 411070
F/6/6/5 | Size, 5000x600x60mm | Nr. | 4 | 33748 | 134992
F/6/6/6 | Size, 5000x500 or 400x60mm | Nr. | 3 | 32272 | 96816
F/6/7 | At 6th/F level
Precast concrete slab
F/6/7/1 | Size, 5100x1200x60mm | Nr. | 106 | 44304 | 4696224
F/6/7/2 | Size, 5100x1100x60mm | Nr. | 2 | 43056 | 86112
F/6/7/3 | Size, 5100x1000x60mm | Nr. | 1 | 41776 | 41776
F/6/7/4 | Size, 5000x800x60mm | Nr. | 6 | 37744 | 226464
F/6/7/5 | Size, 5000x600x60mm | Nr. | 2 | 34086 | 68172
F/6/7/6 | Size, 5000x500 or 400x60mm | Nr. | 2 | 32595 | 65190
F/6/8 | At 7th/F level
Precast concrete slab
F/6/8/1 | Size, 5100x1200x60mm | Nr. | 106 | 44748 | 4743288
F/6/8/2 | Size, 5100x1100x60mm | Nr. | 1 | 43487 | 43487
F/6/8/3 | Size, 5100x1000x60mm | Nr. | 1 | 42194 | 42194
F/6/8/4 | Size, 5000x800x60mm | Nr. | 6 | 38122 | 228732
F/6/8/5 | Size, 5000x600x60mm | Nr. | 2 | 34427 | 68854
F/6/8/6 | Size, 5000x500 or 400x60mm | Nr. | 2 | 32921 | 65842
F/6/9 | At 8th/F level
Precast concrete slab
F/6/9/1 | Size, 5100x1200x60mm | Nr. | 104 | 45196 | 4700384
F/6/9/2 | Size, 5100x1100x60mm | Nr. | 1 | 43922 | 43922
F/6/9/3 | Size, 5100x1000x60mm | Nr. | 1 | 42616 | 42616
F/6/9/4 | Size, 5000x800x60mm | Nr. | 4 | 38504 | 154016
F/6/9/5 | Size, 5000x600x60mm | Nr. | 1 | 34772 | 34772
F/6/9/6 | Size, 5000x500 or 400x60mm | Nr. | 1 | 33251 | 33251
F/7 | Concrete Grade 25 (Ready mixed where necessary) in the following
F/7/1 | From L/G/F level to G/F level.
F/7/1/1 | In Column (C5,300x300mm, single story building) | m3 | 10 | 19392 | 193920
0
F/7/1/2 | In Column (600x600mm ) | m3 | 106 | 19392 | 2055552
0
F/7/1/3 | In shear wall | m3 | 33 | 19392 | 639936
0
F/7/1/4 | Main Beams | m3 | 179 | 19392 | 3471168
0
F/7/1/5 | Peripheral Beams | m3 | 77 | 19392 | 1493184
0
F/7/1/6 | In wall of Lift well | m3 | 63 | 19392 | 1221696
0
F/7/1/7 | Concrete in insitu slab, 125mm thick | m3 | 9 | 19392 | 174528
0
F/7/1/8 | Concrete in insitu slab, 225mm thick, in X-Ray & CT room | m3 | 30 | 19392 | 581760
0
F/7/1/9 | Roof beams in single story area | m3 | 108 | 19392 | 2094336
0
F/7/1/10 | 100mm thick RCC wall on roof slab edge in single story area | m3 | 10 | 19392 | 193920
0
F/7/1/11 | Roof slab in single story area | m3 | 69 | 19392 | 1338048
0
F/7/1/12 | Roof slab in pump room | m3 | 9 | 19392 | 174528
0
F/7/1/13 | Stair case | m3 | 9 | 19392 | 174528
0
F/7/1/14 | 60mm thick top layer in floor slab | m2 | 1884 | 1164 | 2192976
0
F/7/1/15 | Concrete filling between durra board (include additional qty for beams where walls exit above slab) | m3 | 31 | 19392 | 601152
0
F/7/2 | From G/F level to 1st/F level. |  |  | 0
0
F/7/2/1 | In Column | m3 | 224 | 19974 | 4474176
0
F/7/2/2 | In shear wall | m3 | 40 | 19974 | 798960
0
F/7/2/3 | Main Beams | m3 | 179 | 19974 | 3575346
0
F/7/2/4 | Peripheral & other Beams | m3 | 81 | 19974 | 1617894
0
F/7/2/5 | In wall of Lift well | m3 | 46 | 19974 | 918804
0
F/7/2/6 | 225 mm thk. Con. Walls in X-Ray room Etc | m3 | 71 | 19974 | 1418154
0
F/7/2/7 | Concrete in insitu slab, 125mm thick | m3 | 9 | 19974 | 179766
0
F/7/2/8 | Concrete in insitu slab, 225mm thick, in X-Ray & CT room | m3 | 30 | 19974 | 599220
0
F/7/2/9 | Concrete in insitu gutter at porch | m3 | 8 | 19974 | 159792
0
F/7/2/10 | Concrete in pond wall at porch | m3 | 9 | 19974 | 179766
0
F/7/2/11 | Stair case | m3 | 12 | 19974 | 239688
0
F/7/2/12 | Ramp -1 G/F to 1st floor (Flight, side wall& beam) | m3 | 27 | 19974 | 539298
0
F/7/2/13 | Ramp-2 to G/F and floor, at front loby | m3 | 67 | 19974 | 1338258
0
F/7/2/14 | 60mm thick top layer in floor slab | m2 | 1884 | 1200 | 2260800
0
F/7/2/15 | Concrete filling between durra board ( include additional qty for beams where walls exit above slab) | m3 | 32 | 19974 | 639168
0
F/7/3 | From 1st floor level to 2 nd floor slab level. |  |  | 0
0
F/7/3/1 | In Column | m3 | 207 | 20175 | 4176225
0
F/7/3/2 | In shear wall | m3 | 34 | 20175 | 685950
0
F/7/3/3 | Main Beams | m3 | 400 | 20175 | 8070000
0
F/7/3/4 | Peripheral & other Beams | m3 | 157 | 20175 | 3167475
0
F/7/3/5 | In wall of Lift well | m3 | 46 | 20175 | 928050
0
F/7/3/6 | Concrete in insitu slab, 125mm thick | m3 | 80 | 20175 | 1614000
0
F/7/3/7 | Concrete in insitu slab, 225mm thick, in X-Ray & CT room | m3 | 30 | 20175 | 605250
0
F/7/3/8 | 100mm thick RCC wall on roof terrace edge | m3 | 7 | 20175 | 141225
0
F/7/3/9 | Stair case | m3 | 12 | 20175 | 242100
0
F/7/3/10 | 60mm thick top layer in floor slab | m2 | 2834 | 1212 | 3434808
0
F/7/3/11 | Concrete filling between durra board (include additional qty for beams where walls exit above slab) | m3 | 54 | 20175 | 1089450
0
F/7/4 | From 2 nd floor level to 3 rd floor slab level. |  |  | 0
0
F/7/4/1 | In Column | m3 | 152 | 20374 | 3096848
0
F/7/4/2 | In Sheer wall | m3 | 34 | 20374 | 692716
0
F/7/4/3 | Main Beams | m3 | 336 | 20374 | 6845664
0
F/7/4/4 | Peripheral & other Beams | m3 | 160 | 20374 | 3259840
0
F/7/4/5 | In wall of Lift well | m3 | 46 | 20374 | 937204
0
F/7/4/6 | Concrete in insitu slab, 125mm thick | m3 | 126 | 20374 | 2567124
0
F/7/4/7 | 100mm thick RCC wall on roof terrace edge | m3 | 15.4 | 20374 | 313759.6
0
F/7/4/8 | Stair case | m3 | 9 | 20374 | 183366
0
F/7/4/9 | 60mm thick top layer in floor slab | m2 | 2470 | 1225 | 3025750
0
F/7/4/10 | Concrete filling between durra board (include additional qty for beams where walls exit above slab) | m3 | 30 | 20374 | 611220
0
F/7/5 | From 3 rd floor level to 4th floor level. |  |  | 0
0
F/7/5/1 | In Column | m3 | 121 | 20574 | 2489454
0
F/7/5/2 | In Sheer wall | m3 | 30 | 20574 | 617220
0
F/7/5/3 | Main Beams | m3 | 161 | 20574 | 3312414
0
F/7/5/4 | Peripheral & other Beams | m3 | 196 | 20574 | 4032504
0
F/7/5/5 | In wall of Lift well | m3 | 46 | 20574 | 946404
0
F/7/5/6 | Concrete in insitu slab, 125mm thick | m3 | 181 | 20574 | 3723894
0
F/7/5/7 | 100mm thick RCC wall on roof terrace edge | m3 | 9.8 | 20574 | 201625.2
0
F/7/5/8 | Stair case | m3 | 9 | 20574 | 185166
0
F/7/5/9 | 60mm thick top layer in floor slab | m2 | 1586 | 1237 | 1961882
0
F/7/5/10 | Concrete filling between durra board (include additional qty for beams where walls exit above slab) | m3 | 23 | 20574 | 473202
0
F/7/6 | From 4th floor level to 5th floor level. |  |  | 0
0
F/7/6/1 | In Column | m3 | 107 | 20774 | 2222818
0
F/7/6/2 | In shear wall | m3 | 30 | 20774 | 623220
0
F/7/6/3 | Main Beams | m3 | 170 | 20774 | 3531580
0
F/7/6/4 | Peripheral & other Beams | m3 | 87 | 20774 | 1807338
0
F/7/6/5 | In wall of Lift well | m3 | 46 | 20774 | 955604
0
F/7/6/6 | Concrete in insitu slab, 125mm thick | m3 | 43 | 20774 | 893282
0
F/7/6/7 | Stair case | m3 | 9 | 20774 | 186966
0
F/7/6/8 | 60mm thick top layer in floor slab | m2 | 1588 | 1248 | 1981824
0
F/7/6/9 | Concrete filling between durra board (include additional qty for beams where walls exit above slab) | m3 | 25 | 20774 | 519350
0
F/7/7 | From 5th floor level to 6th floor level. |  |  | 0
0
F/7/7/1 | In Column | m3 | 107 | 20972 | 2244004
0
F/7/7/2 | In shear wall | m3 | 30 | 20972 | 629160
0
F/7/7/3 | Main Beams | m3 | 170 | 20972 | 3565240
0
F/7/7/4 | Peripheral & other Beams | m3 | 87 | 20972 | 1824564
0
F/7/7/5 | In wall of Lift well | m3 | 46 | 20972 | 964712
0
F/7/7/6 | Concrete in insitu slab, 125mm thick | m3 | 43 | 20972 | 901796
0
F/7/7/7 | Stair case | m3 | 6 | 20972 | 125832
0
F/7/7/8 | 60mm thick top layer in floor slab | m2 | 1588 | 1260 | 2000880
0
F/7/7/9 | Concrete filling between durra board (include additional qty for beams where walls exit above slab) | m3 | 19.5 | 20972 | 408954
0
F/7/8 | From 6th floor level to 7th floor level. |  |  | 0
0
F/7/8/1 | In Column | m3 | 42 | 21173 | 889266
0
F/7/8/2 | In shear wall | m3 | 30 | 21173 | 635190
0
F/7/8/3 | Main Beams | m3 | 71 | 21173 | 1503283
0
F/7/8/4 | Peripheral & other Beams | m3 | 171 | 21173 | 3620583
0
F/7/8/5 | In wall of Lift well | m3 | 46 | 21173 | 973958
0
F/7/8/6 | Concrete in insitu slab, 125mm thick | m3 | 128 | 21173 | 2710144
0
F/7/8/7 | 100mm thick RCC wall on roof terrace edge | m3 | 21 | 21173 | 444633
0
F/7/8/8 | Stair case | m3 | 6 | 21173 | 127038
0
F/7/8/9 | 60mm thick top layer in floor slab | m2 | 662 | 1272 | 842064
0
F/7/8/10 | Concrete filling between durra board (include additional qty for beams where walls exit above slab) | m3 | 9.5 | 21173 | 201143.5
0
F/7/9 | From 7th floor level to 8th floor level. |  |  | 0
0
F/7/9/1 | In Column | m3 | 42 | 21373 | 897666
0
F/7/9/2 | In Sheer wall | m3 | 30 | 21373 | 641190
0
F/7/9/3 | Main Beams | m3 | 71 | 21373 | 1517483
0
F/7/9/4 | Peripheral & other Beams | m3 | 47 | 21373 | 1004531
0
F/7/9/5 | In wall of Lift well | m3 | 46 | 21373 | 983158
0
F/7/9/6 | Concrete in insitu slab, 125mm thick | m3 | 18 | 21373 | 384714
0
F/7/9/7 | Stair case | m3 | 6 | 21373 | 128238
0
F/7/9/8 | 60mm thick top layer in floor slab | m2 | 662 | 1284 | 850008
0
F/7/9/9 | Concrete filling between durra board (include additional qty for beams where walls exit above slab) | m3 | 9.5 | 21373 | 203043.5
0
F/7/10 | From 8th floor level to roof slab level. |  |  | 0
0
F/7/10/1 | In Column | m3 | 42 | 21572 | 906024
0
F/7/10/2 | In shear wall | m3 | 30 | 21572 | 647160
0
F/7/10/3 | Main Beams | m3 | 71 | 21572 | 1531612
0
F/7/10/4 | Peripheral & other Beams | m3 | 47 | 21572 | 1013884
0
F/7/10/5 | In wall of Lift well | m3 | 46 | 21572 | 992312
0
F/7/10/6 | Concrete in insitu slab, 125mm thick | m3 | 20 | 21572 | 431440
0
F/7/10/7 | Stair case | m3 | 6 | 21572 | 129432
0
F/7/10/8 | 60mm thick top layer in floor slab | m2 | 662 | 1297 | 858614
0
F/7/10/9 | Concrete filling between durra board | m3 | 7 | 21572 | 151004
0
F/7/11 | Roof slab and above roof salb |  |  | 0
0
F/7/11/1 | Concrete in insitu roof slab, 125mm thick | m3 | 129.4 | 21772 | 2817296.8
0
F/7/11/2 | Beams in roof slab | m3 | 51 | 21772 | 1110372
0
F/7/11/3 | 100mm thick RCC wall on roof terrace edge | m3 | 13.3 | 21772 | 289567.6
0
F/7/11/4 | Stair case | m3 | 3 | 21772 | 65316
0
F/7/11/5 | In Column | m3 | 4 | 21772 | 87088
0
F/7/11/6 | Beams | m3 | 7 | 21772 | 152404
0
F/7/11/7 | In wall of Lift well | m3 | 34.5 | 21772 | 751134
0
F/7/11/8 | Concrete in insitu roof slab on mechene room, 125mm thick | m3 | 25.9 | 21772 | 563894.8
0
F/7/11/9 | Stair case | m3 | 3 | 21772 | 65316
0
F/7/12 | Over head water tank, 5.5x14x2 m |  |  | 0
0
F/7/12/1 | Base slab, 300mm thick | m3 | 24 | 21772 | 522528
0
F/7/12/2 | Wall, 250mm thick | m3 | 20 | 21772 | 435440
0
F/7/12/3 | Top slab, 150mm thick including kerb at opening | m3 | 12 | 21772 | 261264
0
F/7/12/4 | Top slab beam , 300x650mm | m3 | 2 | 21772 | 43544
0
F/7/12/5 | Refer Miscellaneous work for other ancillary items in water tank | Note |  | 0
0
| Paddy strow board |  |  | 0
F/8 | Supply and placing Paddy strow board (Durra panels), size, 2440x525x58 mm (mainly) and other size as required. |  |  | 0
| Paddy straw board, size 5100x495 (Durra panels) shall be supply and placed by specified sub contractor (ICC or other supplier approved by consultant). "Rate shall include for gauge 200 polythene wrap around the board" | Note |  | 0 |  | Addendum01
F/8/1 | At G/F level | m2 | 1600 | 1292 | 2067200
F/8/2 | At 1st F/ level | m2 | 2610 | 1306 | 3408660
F/8/3 | At 2nd F/ level | m2 | 1975 | 1319 | 2605025
F/8/4 | At 3rd F/ level | m2 | 1310 | 1331 | 1743610
F/8/5 | At 4th F/ level | m2 | 1390 | 1344 | 1868160
F/8/6 | At 5th F/ level | m2 | 1390 | 1357 | 1886230
F/8/7 | At 6th F/ level | m2 | 575 | 1370 | 787750
F/8/8 | At 7th F/ level | m2 | 575 | 1383 | 795225
F/8/9 | At 8th F/ level | m2 | 550 | 1396 | 767800
F/9 | FORMWORK |  |  | 0
0
F/9 | Sawn timber/ ply wood/ steel formwork to the following |  |  | 0
| Fare face form work shall provide for isolated column, walls, soffit of incitu slabs and beams |  |  | 0
F/9/1 | Form work to Gr. 30 Concrete |  |  | 0
0
| Lower ground floor |  |  | 0 |  |  | 0.97692
0
F/9/1/1 | In pile cap | m2 | 654 | 1026 | 671004
0
F/9/1/2 | In column footing (F1, F2, F3, F4,) | m2 | 86 | 1026 | 88236
0
F/9/1/3 | In ground beam (between pile cap column and under Retain wall) | m2 | 1229 | 1026 | 1260954
0
F/9/1/4 | In retaining wall up to G/F level | m2 | 1260 | 1332 | 1678320
0
F/9/1/5 | In Bottum slab of Lift well | m2 | 17 | 1332 | 22644
0
F/9/1/6 | In walls at lift well up to Lower G/F level | m2 | 144 | 1332 | 191808
0
F/9/1/7 | In Column (300x300mm) up to Lower G/F level | m2 | 27 | 1026 | 27702
0
F/9/1/8 | In Column (600*600mm) up to Lower G/F level | m2 | 164 | 1026 | 168264
0
F/9/1/9 | In Stair footing & wall up to Lower G/F level | m2 | 16 | 1332 | 21312
| Ground floor |  |  | 0
F/9/1/10 | In pile cap | m2 | 212 | 1026 | 217512
0
F/9/1/11 | In column footing (F3, F4,) | m2 | 440 | 1026 | 451440
0
F/9/1/12 | In ground beam (between pile cap and column) | m2 | 1201 | 1026 | 1232226
0
F/9/1/13 | In Column (300x300mm,single story building) | m2 | 41 | 1026 | 42066
0
F/9/1/14 | In Column (450x450mm ) | m2 | 34 | 1026 | 34884
0
F/9/1/15 | In Column (600x600 mm ) | m2 | 152 | 1026 | 155952
0
F/9/1/16 | In Stair footing & wall up to Lower G/F level | m2 | 11 | 1332 | 14652
F/9/2 | Form work to Gr. 35 Concrete
Water sump @ Lower ground floor
F/9/2/1 | Base slab, 350mm thick | m2 | 21 | 1332 | 27972
0
F/9/2/2 | Wall, 250mm thick | m2 | 160 | 1332 | 213120
0
F/9/2/3 | Top slab, 150mm thick including kerb at opening | m2 | 179 | 1332 | 238428
0
F/9/2/4 | Top slab beam , 300x650mm | m2 | 42 | 1332 | 55944
0
F/9/3 | Form work to Gr. 25 Concrete "Rate shall include for center support by propping to pre-cast slab panels once placed on the span beam" |  |  | 0 |  | Addendum01
F/9/3/1 | From L/G/F level to G/F level. |  |  | 0
0
F/9/3/1/1 | In Column (300x300mm, C5,single story building) | m2 | 130 | 1026 | 133380
0
F/9/3/1/2 | In Column (600x600mm,C2, C3, C4, C0 ) | m2 | 712 | 1026 | 730512
0
F/9/3/1/3 | In shear wall | m2 | 263 | 1332 | 350316
0
F/9/3/1/4 | Main Beams | m2 |  | DELETED |  | Addendum 02
F/9/3/1/5 | Peripheral Beams | m2 |  | DELETED |  | Addendum 02
0
F/9/3/1/6 | Roof beams in single story area | m2 | 719 | 1332 | 957708
0
F/9/3/1/7 | 100mm thick RCC wall on roof slab edge in single story area | m2 | 188 | 1332 | 250416
0
F/9/3/1/8 | Roof slab in single story area | m2 | 546 | 1332 | 727272
0
F/9/3/1/9 | In wall of Lift well | m2 | 382 | 1332 | 508824
0
F/9/3/1/10 | 225 mm thk. Con. Walls in X-Ray room Etc | m2 | 2319 | 1332 | 3088908
0
F/9/3/1/11 | Concrete in insitu slab, 125mm thick | m2 | 67 | 1332 | 89244
0
F/9/3/1/12 | Concrete in insitu slab, 225mm thick, in X-Ray & CT room | m2 | 130 | 1332 | 173160
0
F/9/3/1/13 | Stair case | m2 | 60 | 1332 | 79920
0
F/9/3/2 | From G/F level to 1st F level. |  |  | 0
0
F/9/3/2/1 | In Column (450x450 and 600x600 mm ) | m2 | 1456 | 1026 | 1493856
0
F/9/3/2/2 | In shear wall | m2 | 280 | 1332 | 372960
0
F/9/3/2/3 | Main Beams | m2 | 905 | 1422 | 1286910
0
F/9/3/2/4 | Peripheral Beams | m2 | 436 | 1422 | 619992
0
F/9/3/2/5 | In wall of Lift well | m2 | 375 | 1332 | 499500
0
F/9/3/2/6 | 225 mm thk. Con. Walls in X-Ray room Etc | m2 | 736 | 1332 | 980352
0
F/9/3/2/7 | Concrete in insitu slab, 125mm thick | m2 | 170 | 1332 | 226440
0
F/9/3/2/8 | Concrete in insitu slab, 225mm thick, in X-Ray & CT room | m2 | 129 | 1332 | 171828
0
F/9/3/2/9 | Concrete in insitu gutter at porch | m2 | 65 | 1332 | 86580
0
F/9/3/2/10 | Concrete in pond wall at porch | m2 | 77 | 1332 | 102564
0
F/9/3/2/11 | Stair case | m2 | 80 | 1332 | 106560
0
F/9/3/2/12 | Ramp -1 G/F to 1st floor (Flight, side wall& beam) | m2 | 303 | 1332 | 403596
0
F/9/3/2/13 | Ramp-2 to G/F and floor, at front loby | m2 | 143 | 1332 | 190476
0
F/9/3/3 | From 1st floor level to 2 nd floor slab level. |  |  | 0
0
F/9/3/3/1 | In Column (450x450 and 600x600 mm ) | m2 | 1378 | 1043 | 1437254
0
F/9/3/3/2 | In shear wall | m2 | 280 | 1356 | 379680
0
F/9/3/3/3 | Main Beams | m2 | 1300 | 1598 | 2077400
0
F/9/3/3/4 | Peripheral Beams | m2 | 586 | 1598 | 936428
0
F/9/3/3/5 | In wall of Lift well | m2 | 375 | 1356 | 508500
0
F/9/3/3/6 | Concrete in insitu slab, 125mm thick | m2 | 492 | 1356 | 667152
0
F/9/3/3/7 | Concrete in insitu slab, 225mm thick, in X-Ray & CT room | m2 | 129 | 1356 | 174924
0
F/9/3/3/8 | 100mm thick RCC wall on roof slab edge in single story area | m2 | 140 | 1356 | 189840
0
F/9/3/3/9 | Stair case | m2 | 80 | 1356 | 108480
0
F/9/3/4 | From 2 nd floor level to 3 rd floor slab level. |  |  | 0
0
F/9/3/4/1 | In Column (450x450 and 600x600 mm ) | m2 | 1020 | 1061 | 1082220
0
F/9/3/4/2 | In shear wall | m2 | 280 | 1379 | 386120
0
F/9/3/4/3 | Main Beams | m2 | 1100 | 1627 | 1789700
0
F/9/3/4/4 | Peripheral Beams | m2 | 598 | 1627 | 972946
0
F/9/3/4/5 | In wall of Lift well | m2 | 375 | 1379 | 517125
0
F/9/3/4/6 | Insitu RCC floor slab | m2 | 1002 | 1379 | 1381758
0
F/9/3/4/7 | 100mm thick RCC wall on roof slab edge in single story area | m2 | 308 | 1379 | 424732
0
F/9/3/4/8 | Stair case | m2 | 60 | 1379 | 82740
0
F/9/3/5 | From 3 rd floor level to 4th floor level. |  |  | 0
0
F/9/3/5/1 | In Column (450x450 and 600x600 mm ) | m2 | 807 | 1079 | 870753
0
F/9/3/5/2 | In shear wall | m2 | 250 | 1403 | 350750
0
F/9/3/5/3 | Main Beams | m2 | 450 | 1655 | 744750
0
F/9/3/5/4 | Peripheral Beams | m2 | 1008 | 1655 | 1668240
0
F/9/3/5/5 | In wall of Lift well | m2 | 375 | 1403 | 526125
0
F/9/3/5/6 | Insitu RCC floor slab | m2 | 1437 | 1403 | 2016111
0
F/9/3/5/7 | 100mm thick RCC wall on roof slab edge in single story area | m2 | 196 | 1403 | 274988
0
F/9/3/5/8 | Stair case | m2 | 60 | 1403 | 84180
0
F/9/3/6 | From 4 th floor level to 5 th floor level. |  |  | 0
0
F/9/3/6/1 | In Column (450x450 and 600x600 mm ) | m2 | 708 | 1096 | 775968
0
F/9/3/6/2 | In shear wall | m2 | 250 | 1427 | 356750
0
F/9/3/6/3 | Main Beams | m2 | 560 | 1684 | 943040
0
F/9/3/6/4 | Peripheral Beams | m2 | 431 | 1684 | 725804
0
F/9/3/6/5 | In wall of Lift well | m2 | 375 | 1427 | 535125
0
F/9/3/6/6 | Insitu RCC floor slab | m2 | 342 | 1427 | 488034
0
F/9/3/6/7 | Stair case | m2 | 60 | 1427 | 85620
0
F/9/3/7 | From 5 th floor level to 6 th floor level. |  |  | 0
0
F/9/3/7/1 | In Column (450x450 and 600x600 mm ) | m2 | 708 | 1114 | 788712
0
F/9/3/7/2 | In shear wall | m2 | 250 | 1451 | 362750
0
F/9/3/7/3 | Main Beams | m2 | 560 | 1712 | 958720
0
F/9/3/7/4 | Peripheral Beams | m2 | 431 | 1712 | 737872
0
F/9/3/7/5 | In wall of Lift well | m2 | 375 | 1451 | 544125
0
F/9/3/7/6 | Insitu RCC floor slab | m2 | 342 | 1451 | 496242
0
F/9/3/7/7 | Stair case | m2 | 40 | 1451 | 58040
0
F/9/3/8 | From 6 th floor level to 7 th floor level. |  |  | 0
0
F/9/3/8/1 | In Column (450x450 and 600x600 mm ) | m2 | 280 | 1131 | 316680
0
F/9/3/8/2 | In shear wall | m2 | 250 | 1474 | 368500
0
F/9/3/8/3 | Main Beams | m2 | 215 | 1740 | 374100
0
F/9/3/8/4 | Peripheral Beams | m2 | 865 | 1740 | 1505100
0
F/9/3/8/5 | In wall of Lift well | m2 | 375 | 1474 | 552750
0
F/9/3/8/6 | Insitu RCC floor slab | m2 | 1000 | 1474 | 1474000
0
F/9/3/8/7 | 100mm thick RCC wall on roof slab edge in single story area | m2 | 420 | 1474 | 619080
0
F/9/3/8/8 | Stair case | m2 | 40 | 1474 | 58960
0
F/9/3/9 | From 7 th floor level to 8 th floor level. |  |  | 0
0
F/9/3/9/1 | In Column (450x450 and 600x600 mm ) | m2 | 280 | 1149 | 321720
0
F/9/3/9/2 | In shear wall | m2 | 250 | 1498 | 374500
0
F/9/3/9/3 | Main Beams | m2 | 215 | 1768 | 380120
0
F/9/3/9/4 | Peripheral Beams | m2 | 228 | 1768 | 403104
0
F/9/3/9/5 | In wall of Lift well | m2 | 375 | 1498 | 561750
0
F/9/3/9/6 | Insitu RCC floor slab | m2 | 144 | 1498 | 215712
0
F/9/3/9/7 | Stair case | m2 | 40 | 1498 | 59920
0
F/9/3/10 | From 8 th floor level to roof slab level. |  |  | 0
0
F/9/3/10/1 | In Column (450x450 and 600x600 mm ) | m2 | 280 | 1166 | 326480
0
F/9/3/10/2 | In shear wall | m2 | 250 | 1522 | 380500
0
F/9/3/10/3 | Main Beams | m2 | 215 | 1798 | 386570
0
F/9/3/10/4 | Peripheral Beams | m2 | 228 | 1798 | 409944
0
F/9/3/10/5 | In wall of Lift well | m2 | 375 | 1522 | 570750
0
F/9/3/10/6 | Insitu RCC floor slab | m2 | 159 | 1522 | 241998
0
F/9/3/10/7 | Stair case | m2 | 22 | 1522 | 33484
0
F/9/3/11 | Roof slab and above roof slab |  |  | 0
0
F/9/3/11/1 | Concrete in insitu roof slab, 125mm thick | m2 | 1035 | 1545 | 1599075
0
F/9/3/11/2 | Beams in roof slab | m2 | 444 | 1545 | 685980
0
F/9/3/11/3 | 100mm thick RCC wall on roof slab edge in single story area | m2 | 266 | 1545 | 410970
0
F/9/3/11/4 | Stair case | m2 | 20 | 1545 | 30900
0
F/9/3/11/5 | In Column | m2 | 32 | 1037 | 33184
0
F/9/3/11/6 | Beams | m2 | 59 | 1545 | 91155
0
F/9/3/11/7 | In wall of Lift well | m2 | 35 | 1545 | 54075
0
F/9/3/11/8 | Concrete in insitu roof slab on mechene room, 125mm thick | m2 | 207 | 1545 | 319815
0
F/9/3/11/9 | Stair case | m2 | 20 | 1545 | 30900
0
F/9/3/12 | Over head water tank, 5.5x14x2 m |  |  | 0
0
F/9/3/12/1 | Base slab, 300mm thick | m2 | 89 | 1569 | 139641
0
F/9/3/12/2 | Wall, 250mm thick | m2 | 156 | 1569 | 244764
0
F/9/3/12/3 | Top slab, 150mm thick including kerb at opening | m2 | 83 | 1569 | 130227
0
F/9/3/12/4 | Top slab beam , 300x650mm | m2 | 11 | 1569 | 17259
0
F/10 | REINFORCEMENT (R/F) |  |  | 0
0
F/10 | Furnish, fabricate, place and tie high yield R/F bars with characteristic strength 460N/mm2 including binding wire, cover and spacer blocks complete in sizes varying from Y10 to Y25 |  |  | 0
0
F/10/1 | Reinforcement in Gr.30 concrete |  |  | 0
| Lower ground floor |  |  | 0
0
F/10/1/1 | In pile cap | Kg | 21630 | 195 | 4217850
0
F/10/1/2 | In column footing (F1, F2, F3, F4,) | Kg | 2069 | 195 | 403455
0
F/10/1/3 | In ground beam & sheer wall footing (between pile cap column and under Retain wall) | Kg | 36161 | 195 | 7051395
0
F/10/1/4 | In retaining wall up to G/F level | Kg | 14564 | 195 | 2839980
0
F/10/1/5 | In Bottum slab of Lift well | Kg | 2221 | 195 | 433095
0
F/10/1/6 | In walls at lift well up to Lower G/F level | Kg | 2030 | 195 | 395850
0
F/10/1/7 | In Column (300x300mm,single story building) | Kg | 676 | 195 | 131820
0
F/10/1/8 | In Column (600x600 mm ) | Kg | 13095 | 195 | 2553525
0
F/10/1/9 | In Stair footing & wall up to Lower G/F level | Kg | 258 | 195 | 50310
0
F/10/2 | Ground floor |  |  | 0
0
F/10/2/1 | In pile cap | Kg | 6655 | 195 | 1297725
0
F/10/2/2 | In column footing (F3, F4,) | Kg | 13460 | 195 | 2624700
0
F/10/2/3 | In ground beam (between pile cap and column) | Kg | 33295 | 195 | 6492525
0
F/10/2/4 | In Column (300x300mm,single story building) | Kg | 1428 | 195 | 278460
0
F/10/2/5 | In Column (450x450mm ) | Kg | 1032 | 195 | 201240
0
F/10/2/6 | In Column (600x600 mm ) | Kg | 6215 | 195 | 1211925
0
F/10/2/7 | In Stair footing & wall up to G/F level | Kg | 172 | 195 | 33540
0
F/10/3 | Reinforcement in Gr.25 concrete |  |  | 0
0
F/10/3/1 | From L/G/F level to G/F level. |  |  | 0
0
F/10/3/1/1 | In Column (C5,300x300mm, single story building) | Kg | 1300 | 195 | 253500
0
F/10/3/1/2 | In Column (600x600mm ) | Kg | 28333 | 195 | 5524935
0
F/10/3/1/3 | In shear wall | Kg | 3432 | 195 | 669240
0
F/10/3/1/4 | Main Beams (R/F for Ad. Beam under wall exit at P.C. panel include) | Kg | 23814 | 195 | 4643730
0
F/10/3/1/5 | Peripheral Beams | Kg | 20786 | 195 | 4053270
0
F/10/3/1/6 | In wall of Lift well | Kg | 6528 | 195 | 1272960
0
F/10/3/1/7 | Concrete in insitu slab, 125mm thick | Kg | 855 | 195 | 166725
0
F/10/3/1/8 | Roof beams in single story area | Kg | 12939 | 195 | 2523105
0
F/10/3/1/9 | 100mm thick RCC wall on roof slab edge in single story area | Kg | 1316 | 195 | 256620
0
F/10/3/1/10 | Roof slab in single story area | Kg | 7167 | 195 | 1397565
0
F/10/3/1/11 | Roof slab in pump room | Kg | 1018 | 195 | 198510
0
F/10/3/1/12 | Stair case | Kg | 600 | 195 | 117000
0
| Water sump @ Lower ground floor |  |  | 0
F/10/3/1/13 | Base slab, 350mm thick | Kg | 3661 | 195 | 713895
0
F/10/3/1/14 | Wall, 250mm thick | Kg | 6596 | 195 | 1286220
0
F/10/3/1/15 | Top slab, 150mm thick including kerb at opening | Kg | 3376 | 195 | 658320
0
F/10/3/1/16 | Top slab beam , 300x650mm | Kg | 826 | 195 | 161070
0
F/10/3/2 | From G/F level to 1st/F level. |  |  | 0
0
F/10/3/2/1 | In Column | Kg | 60079 | 195 | 11715405
0
F/10/3/2/2 | In shear wall | Kg | 4170 | 195 | 813150
0
F/10/3/2/3 | Main Beams (R/F for Ad. Beam under wall exit at P.C. panel include) | Kg | 23814 | 195 | 4643730
0
F/10/3/2/4 | Peripheral Beams | Kg | 19278 | 195 | 3759210
0
F/10/3/2/5 | In wall of Lift well | Kg | 4830 | 195 | 941850
0
F/10/3/2/6 | 225 mm thk. Con. Walls in X-Ray room Etc | Kg | 5279 | 195 | 1029405
0
F/10/3/2/7 | Concrete in insitu slab, 125mm thick | Kg | 855 | 195 | 166725
0
F/10/3/2/8 | Concrete in insitu gutter at porch | Kg | 945 | 195 | 184275
0
F/10/3/2/9 | Concrete in pond wall at porch | Kg | 951 | 195 | 185445
0
F/10/3/2/10 | Stair case | Kg | 800 | 195 | 156000
0
F/10/3/2/11 | Ramp -1 G/F to 1st floor (Flight, side wall& beam) | Kg | 27 | 195 | 5265
0
F/10/3/2/12 | Ramp-2 to G/F and floor, at front loby | Kg | 67 | 195 | 13065
0
F/10/3/3 | From 1st floor level to 2 nd floor slab level. |  |  | 0
0
F/10/3/3/1 | In Column | Kg | 55683 | 199 | 11080917
0
F/10/3/3/2 | In shear wall | Kg | 3518 | 199 | 700082
0
F/10/3/3/3 | Main Beams (R/F for Ad. Beam under wall exit at P.C. panel include) | Kg | 53424 | 199 | 10631376
0
F/10/3/3/4 | Peripheral Beams | Kg | 37247 | 199 | 7412153
0
F/10/3/3/5 | In wall of Lift well | Kg | 4830 | 199 | 961170
0
F/10/3/3/6 | Concrete in insitu slab, 125mm thick | Kg | 8240 | 199 | 1639760
0
F/10/3/3/7 | Concrete in insitu slab, 225mm thick, in X-Ray & CT room | Kg | 1742 | 199 | 346658
0
F/10/3/3/8 | 100mm thick RCC wall on roof slab edge in single story area | Kg | 420 | 199 | 83580
0
F/10/3/3/9 | Stair case | Kg | 800 | 199 | 159200
0
F/10/3/4 | From 2 nd floor level to 3 rd floor slab level. |  |  | 0
0
F/10/3/4/1 | In Column | Kg | 40888 | 203 | 8300264
0
F/10/3/4/2 | In shear wall | Kg | 3518 | 203 | 714154
0
F/10/3/4/3 | Main Beams (R/F for Ad. Beam under wall exit at P.C. panel include) | Kg | 44877 | 203 | 9110031
0
F/10/3/4/4 | Peripheral Beams | Kg | 38080 | 203 | 7730240
0
F/10/3/4/5 | In wall of Lift well | Kg | 4830 | 203 | 980490
0
F/10/3/4/6 | Concrete in insitu slab, 125mm thick | Kg | 12978 | 203 | 2634534
0
F/10/3/4/7 | 100mm thick RCC wall on roof slab edge in single story area | Kg | 924 | 203 | 187572
0
F/10/3/4/8 | Stair case | Kg | 600 | 203 | 121800
0
F/10/3/5 | From 3 rd floor level to 4th floor level. |  |  | 0
0
F/10/3/5/1 | In Column | Kg | 32549 | 207 | 6737643
0
F/10/3/5/2 | In shear wall | Kg | 3150 | 207 | 652050
0
F/10/3/5/3 | Main Beams (R/F for Ad. Beam under wall exit at P.C. panel include) | Kg | 21504 | 207 | 4451328
0
F/10/3/5/4 | Peripheral Beams | Kg | 46529 | 207 | 9631503
0
F/10/3/5/5 | In wall of Lift well | Kg | 4830 | 207 | 999810
0
F/10/3/5/6 | Concrete in insitu slab, 125mm thick | Kg | 18643 | 207 | 3859101
0
F/10/3/5/7 | 100mm thick RCC wall on roof slab edge in single story area | Kg | 588 | 207 | 121716
0
F/10/3/5/8 | Stair case | Kg | 600 | 207 | 124200
0
F/10/3/6 | From 4th floor level to 5th floor level. |  |  | 0
0
F/10/3/6/1 | In Column | Kg | 28783 | 211 | 6073213
0
F/10/3/6/2 | In shear wall | Kg | 3150 | 211 | 664650
0
F/10/3/6/3 | Main Beams (R/F for Ad. Beam under wall exit at P.C. panel include) | Kg | 22706 | 211 | 4790966
0
F/10/3/6/4 | Peripheral Beams | Kg | 20635 | 211 | 4353985
0
F/10/3/6/5 | In wall of Lift well | Kg | 4830 | 211 | 1019130
0
F/10/3/6/6 | Concrete in insitu slab, 125mm thick | Kg | 4429 | 211 | 934519
0
F/10/3/6/7 | Stair case | Kg | 600 | 211 | 126600
0
F/10/3/7 | From 5th floor level to 6th floor level. |  |  | 0
0
F/10/3/7/1 | In Column | Kg | 28783 | 214 | 6159562
0
F/10/3/7/2 | In shear wall | Kg | 3150 | 214 | 674100
0
F/10/3/7/3 | Main Beams (R/F for Ad. Beam under wall exit at P.C. panel include) | Kg | 22706 | 214 | 4859084
0
F/10/3/7/4 | Peripheral Beams | Kg | 20587 | 214 | 4405618
0
F/10/3/7/5 | In wall of Lift well | Kg | 4830 | 214 | 1033620
0
F/10/3/7/6 | Concrete in insitu slab, 125mm thick | Kg | 4429 | 214 | 947806
0
F/10/3/7/7 | Stair case | Kg | 400 | 214 | 85600
0
F/10/3/8 | From 6th floor level to 7th floor level. |  |  | 0
F/10/3/8/1 | In Column | Kg | 11298 | 218 | 2462964
0
F/10/3/8/2 | In shear wall | Kg | 3150 | 218 | 686700
0
F/10/3/8/3 | Main Beams (R/F for Ad. Beam under wall exit at P.C. panel include) | Kg | 9483 | 218 | 2067294
0
F/10/3/8/4 | Peripheral Beams | Kg | 40579 | 218 | 8846222
0
F/10/3/8/5 | In wall of Lift well | Kg | 4830 | 218 | 1052940
0
F/10/3/8/6 | Concrete in insitu slab, 125mm thick | Kg | 13184 | 218 | 2874112
0
F/10/3/8/7 | 100mm thick RCC wall on roof slab edge in single story area | Kg | 1260 | 218 | 274680
0
F/10/3/8/8 | Stair case | Kg | 420 | 218 | 91560
0
F/10/3/9 | From 7th floor level to 8th floor level. |  |  | 0
0
F/10/3/9/1 | In Column | Kg | 11298 | 222 | 2508156
0
F/10/3/9/2 | In shear wall | Kg | 3150 | 222 | 699300
0
F/10/3/9/3 | Main Beams (R/F for Ad. Beam under wall exit at P.C. panel include) | Kg | 9483 | 222 | 2105226
0
F/10/3/9/4 | Peripheral Beams | Kg | 11067 | 222 | 2456874
0
F/10/3/9/5 | In wall of Lift well | Kg | 4830 | 222 | 1072260
0
F/10/3/9/6 | Concrete in insitu slab, 125mm thick | Kg | 1854 | 222 | 411588
0
F/10/3/9/7 | Stair case | Kg | 420 | 222 | 93240
0
F/10/3/10 | From 8th floor level to roof slab level. |  |  | 0
0
F/10/3/10/1 | In Column | Kg | 11298 | 226 | 2553348
0
F/10/3/10/2 | In shear wall | Kg | 3150 | 226 | 711900
0
F/10/3/10/3 | Main Beams (R/F for Ad. Beam under wall exit at P.C. panel include) | Kg | 9483 | 226 | 2143158
0
F/10/3/10/4 | Peripheral Beams | Kg | 11067 | 226 | 2501142
0
F/10/3/10/5 | In wall of Lift well | Kg | 4830 | 226 | 1091580
0
F/10/3/10/6 | Concrete in insitu slab, 125mm thick | Kg | 2060 | 226 | 465560
0
F/10/3/10/7 | Stair case | Kg | 220 | 226 | 49720
0
F/10/3/11 | Roof slab and above roof salb |  |  | 0
0
F/10/3/11/1 | Concrete in insitu roof slab, 125mm thick | Kg | 13585 | 230 | 3124550
0
F/10/3/11/2 | Beams in roof slab | Kg | 11706 | 230 | 2692380
0
F/10/3/11/3 | 100mm thick RCC wall on roof slab edge in single story area | Kg | 798 | 230 | 183540
0
F/10/3/11/4 | Stair case | Kg | 180 | 230 | 41400
0
| Above roof slab |  |  | 0
F/10/3/11/5 | In Column | Kg | 851 | 233 | 198283
0
F/10/3/11/6 | Beams | Kg | 1522 | 233 | 354626
0
F/10/3/11/7 | In wall of Lift well | Kg | 3554 | 233 | 828082
0
F/10/3/11/8 | Concrete in insitu roof slab on machine room, 125mm thick | Kg | 2717 | 233 | 633061
0
F/10/3/11/9 | Stair case | Kg | 180 | 233 | 41940
0
| Over head water tank, 5.5x14x2 m |  |  | 0
F/10/3/11/10 | Base slab, 300mm thick | Kg | 1294 | 233 | 301502
0
F/10/3/11/11 | Wall, 250mm thick | Kg | 3218 | 233 | 749794
0
F/10/3/11/12 | Top slab, 150mm thick including kerb at opening | Kg | 1551 | 233 | 361383
0
F/10/3/11/13 | Top slab beam , 300x650mm | Kg | 207 | 233 | 48231
0
F/11 | Furnish, fabricate, place and tie Mild steel R/F with characteristic strength, 250 N/mm2. Rate shall include for binding wire, cover spacer blocks complete in size varying from R6 to R10 in the following |  |  | 0
0
F/11/1 | For column from ground level to 3rd floor level. (Provisional qty.) | Kg | 100 | 203 | 20300
0
F/11/2 | Supply and laying of BRC mesh, A-98 (5mm dia. 200 x 200mm) | m2 | 12000 | 565 | 6780000 | Addendum01
| TOTAL CARRIED TO SUMMARY |  |  |  | 627880545.816
Note on F1014: Dilini: Change - Binali 17/04/2013

## masonry
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
BILL OF QUANTITIES |  | MASONRY WORK
ITEM NO | DESCRIPTION | UNIT | QTY. | RATE (RS) | AMOUNT (RS)
G | MASONRY WORK
G/1 | Random rubble masonry in cement and sand 1:8 using 150mm to 225mm size broken stone (Provisional quantity) | m3 | 50 | 8777 | 438850
Brick walls in burn clay bricks, size, 225x112x75mm in cement & sand 1:8 in the following.
G/2 | 225mm thick walls
G/2/1 | Lower ground floor level to ground floor level | m2 | 3177 | 2418 | 7681986
G/2/2 | Mezzanine floor | m2 | 63 | 2418 | 152334
G/2/3 | Ground floor level to first floor level | m2 | 3322 | 2418 | 8032596
G/2/4 | 1st floor level to 2nd floor level | m2 | 2126 | 2467 | 5244842
G/2/5 | 2nd floor level to 3rd floor level | m2 | 2026 | 2515 | 5095390
G/2/6 | 3rd floor level to 4th floor level | m2 | 1535 | 2564 | 3935740
G/2/7 | 4th floor level to 5th floor level | m2 | 1193 | 2612 | 3116116
G/2/8 | 5th floor level to 6th floor level | m2 | 1264 | 2660 | 3362240
G/2/9 | 6thfloor level to 7th floor level | m2 | 740 | 2709 | 2004660
G/2/10 | 7thfloor level to 8th floor level | m2 | 732 | 2757 | 2018124
G/2/11 | Above 8th floor level | m2 | 742 | 2805 | 2081310
Pump room, Machine Room
G/2/12 | Pump room on water sump at lower ground floor level | m2 | 82 | 2418 | 198276
G/2/13 | Machine Room on roof slab | m2 | 133 | 2854 | 379582
G/3 | 112.5mm thick walls
| Rate shall include for provision of stiffener column, size, 100x112mm, with 2T- 10 R/F bars and horizontal pad, size, 112x40mm,with 2R- 6 R/F bars to walls exceeding 2m in height and 3m in length (unless braced by another cross wall) | Note
G/3/1 | Lower ground floor to ground floor level | m2 | 1147 | 1782 | 2043954
G/3/2 | Mezzanine floor | m2 | 148 | 1782 | 263736
G/3/3 | Ground floor level to first floor level | m2 | 1489 | 1782 | 2653398
G/3/4 | 1st floor level to 2nd floor level | m2 | 1209 | 1818 | 2197962
G/3/5 | 2nd floor level to 3rd floor level | m2 | 2470 | 1854 | 4579380
G/3/6 | 3rd floor level to 4th floor level | m2 | 918 | 1854 | 1701972
G/3/7 | 4th floor level to 5th floor level | m2 | 1241 | 1925 | 2388925
G/3/8 | 5th floor level to 6th floor level | m2 | 1228 | 1961 | 2408108
G/3/9 | 6thfloor level to 7th floor level | m2 | 642 | 1996 | 1281432
G/3/10 | 7thfloor level to 8th floor level | m2 | 645 | 2032 | 1310640
G/3/11 | Above 8th floor level | m2 | 553 | 2103 | 1162959
| TOTAL CARRIED TO SUMMARY |  |  | Rs | 65734512

## W.proof
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
BILL OF QUANTITIES |  | WATER PROOFING
ITEM NO | DESCRIPTION | UNIT | QTY. | RATE (RS) | AMOUNT (RS)
H/- | WATER PROOFING
H/1 | Provide vapor barrier comprising 500g polythene membrane on top of compacted and prepared fill under floors. All joints shall be lapped at least 150mm and shall be included in to rate.
H/1/1 | In Lower G/F | m2 | 3292 | 96 | 316032
H/1/2 | In Lower G/F, retain wall | m2 | 554 | 96 | 53184
H/1/3 | In G/F | m2 | 1637 | 96 | 157152
H/2 | Water proofing in toilets / bathrooms floors & walls up to 2.1m height with "Baralastic" or equalent approved type waterproofing compound. All as per the manufacture's specification & to the Engineer's approval.
| Screed for tiling will be protective screed for above water proofing.. | Note
H/2/1 | in Lower ground floor | m2 | 390 | 1437 | 560430
H/2/2 | in Mezzanine floor | m2 | 66 | 1437 | 94842
H/2/3 | in ground floor | m2 | 362 | 1437 | 520194
H/2/4 | in first floor | m2 | 681 | 1452 | 988812
H/2/5 | in 2 nd floor | m2 | 630 | 1466 | 923580
H/2/6 | in 3 rd floor | m2 | 1012 | 1481 | 1498772
H/2/7 | in 4 th floor | m2 | 897 | 1495 | 1341015
H/2/8 | in 5 th floor | m2 | 492 | 1509 | 742428
H/2/9 | in 6 th floor | m2 | 400 | 1524 | 609600
H/2/10 | in 7 th floor | m2 | 428 | 1538 | 658264
H/2/11 | in 8 th floor | m2 | 298 | 1552 | 462496
H/2/12 | in Floor slab at Lower ground floor (Provisional Qty) | m2 | 50 | 1437 | 71850
H/2/13 | in retain wall at Lower ground floor (Provisional Qty) | m2 | 50 | 1437 | 71850
H/3 | WATER FROOFING AND THERMAL INSIULATION IN ROOF SLABS
Refer Drawing : HB/ST/42/T
All water proofing shall continue up to 200mm at adjoining walls/columns etc.
H/3 | Provide even surfaced sloping screed (Thickness varies from 125 to 40mm ) in Gr. 20 concrete on roof slab. Slope shall be kept towards to rain water outlets.
H/3/1 | In single story building at Lower G/F | m2 | 608 | 1200 | 729600
H/3/2 | In 1st floor slab level | m2 | 228 | 1224 | 279072
H/3/3 | In 2nd floor slab level | m2 | 737 | 1248 | 919776
H/3/4 | In 3rd floor slab level | m2 | 1280 | 1272 | 1628160
H/3/5 | In 6th floor slab level | m2 | 1503 | 1344 | 2020032
H/3/6 | In roof slab level | m2 | 1090 | 1392 | 1517280
H/3/7 | In machine room roof slab | m2 | 147 | 1416 | 208152
H/4 | Water proofing with "Radcon " or equalent type approved quality & manufacture in roof terrace, & balcony . Rate shall include for relevant arrangement to proper connection with rain water drainage outlets and filling with mastic sealant where necessary .
H/4/1 | In single story building at Lower G/F | m2 | 608 | 1772 | 1077376
H/4/2 | In 1st floor slab level | m2 | 258 | 1790 | 461820
H/4/3 | In 2nd floor slab level | m2 | 737 | 1808 | 1332496
H/4/4 | In 3rd floor slab level | m2 | 1280 | 1826 | 2337280
H/4/5 | In 6th floor slab level | m2 | 1503 | 1879 | 2824137
H/4/6 | In roof slab level | m2 | 1090 | 1914 | 2086260
H/4/7 | In machine room roof slab | m2 | 147 | 1932 | 284004
H/5 | Provide Thermal insulation, 50mm thick extruded polystyrene insulation board (isobond or equivalent board)as per manufacture's specification, separation layer (500 gauge polythene) and protective screed (40mm thk. Gr.20 Concrete, r/forced with 50x50m wire mesh) comprising with expansion joint at 3 m interval ( 10x25mm grove filled with asphalt ) Rate shall include for relevant arrangement or proper connection to rain water drainage outlets and filling with mastic sealant where necessary .
H/5/1 | In single story building at Lower G/F | m2 | 608 | 3949 | 2400992
H/5/2 | In 1st floor slab level | m2 | 228 | 4028 | 918384
H/5/3 | In 2nd floor slab level | m2 | 737 | 4107 | 3026859
H/5/4 | In 3rd floor slab level | m2 | 1280 | 4186 | 5358080
H/5/5 | In 6th floor slab level | m2 | 1503 | 4423 | 6647769
H/5/6 | In roof slab level | m2 | 1090 | 4581 | 4993290
H/5/7 | In machine room roof slab | m2 | 147 | 4660 | 685020
H/6 | Providing Water proofing "Xypex" or equalent approved type waterproofing compound. All as per the manufacture's specification & to the Engineer's approval.
H/6/1 | in water sump base | m2 | 170 | 1241 | 210970
H/6/2 | in water sump wall | m2 | 133 | 1241 | 165053
H/6/3 | Providing sloping screed to base slab with maintaining of slope, 1:200 towards collecting pit (75mm maximum thick in Gr.20 Concrete) | m2 | 170 | 900 | 153000
H/7 | Provide Damp Proof Course on top of RR masonry foundations comprising 18mm thick screed in cement and sand 1:3 with two applications of penetration asphalt laid hot/DPC tar and blinding sand . Provisional quantity) | m2 | 50 | 678 | 33900
| TOTAL CARRIED TO SUMMARY |  |  | Rs. | 51369263

## Metal wk
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
BILL OF QUANTITIES |  | METAL WORK
ITEM NO | DESCRIPTION | UNIT | QTY. | RATE (RS) | AMOUNT (RS)
K | METAL WORK
Note:
1) All doors, windows & partitions items described hereunder shall be fabricated in matt finished anodized Aluminium (avarage coating thickness, 15 micrones + or - 2micrones) extrusions conforming in all respects to the specification and detail drawings.
2) Each door and window sash shall be fitted with the accessories indicated in the specification/ schedule/BOQ and no extra payment what so ever will be made for any standard fittings and accessories even if such are not incorporated in the specification, schedule and detail drawings.
3) The items described hereinafter indicate only the types and sizes of the doors and windows together with a very brief description thereof. Particulars should be obtained by reference to the specification, schedule and detail drawings.
4) Glazing for all windows and fanlights shall be 5mm thick tinted float glass and for doors shall be 5mm thick clear float glass. Paneling shall consist of 3mm thick powder coated aluminum sheeting or 3mm thick laminated sheets as specified.
5) Sample for door/ window sash and all accessories with shop drawing to be approved by the Engineer
6) Indication for major materials to be used as follows
Aluminum - Lanka Aluminum Sating Finished (15 Mc ) or Equivalent
Gaskets - Sunplast gasket or Equivalent
Silicone - last gasket or Equivalent
Screws - Stainless steel
Door lock - Alfa or Equivalent
Friction Stayers - Stainless steel CDM or Equivalent
Butt Hinges - 4''x3'' Stainless steel
DOORS AND WINDOWS
Furnish, fabricate and install aluminum frame glazed windows of the types and overall sizes specified hereinafter in conformity with the specification, schedule and detail mentioned in the drawings
WINDOWS
Refer Dwg. No: HB/AR/21/T
K/1 | Aluminum Window, comprising with sash (Aluminum frame, 5mm thick glass (G) and Al. louvers (L)) and aluminum frame shall be as per the drawing. Rate shall include for hinges, casement fasting and casement staying arrangement.
K/1/1 | Window type W1 overall size 6400mm x 2800mm,
K/1/1/1 | in 4 th floor | Nos. | 1 | 264942 | 264942
K/1/1/2 | in 5 th floor | Nos. | 1 | 264942 | 264942
K/1/1/3 | in 6 th floor | Nos. | 1 | 264942 | 264942
K/1/1/4 | in 7 th floor | Nos. | 2 | 264942 | 529884
K/1/1/5 | in 8 th floor | Nos. | 2 | 264942 | 529884
K/1/2 | Window type W2 overall size 6400mm x 1750mm
K/1/2/1 | in L/G/ floor | Nos. | 2 | 121257 | 242514
K/1/2/2 | in G/ floor | Nos. | 1 | 121257 | 121257
K/1/2/3 | in 1st floor | Nos. | 1 | 121257 | 121257
K/1/2/4 | in 2nd floor | Nos. | 1 | 121257 | 121257
K/1/2/5 | in 3rd floor | Nos. | 7 | 121257 | 848799
K/1/2/6 | in 4th floor | Nos. | 2 | 121257 | 242514
K/1/2/7 | in 5th floor | Nos. | 4 | 121257 | 485028
K/1/2/8 | in 6th floor | Nos. | 1 | 121257 | 121257
K/1/2/9 | in 7th floor | Nos. | 1 | 121257 | 121257
K/1/2/10 | in 8th floor | Nos. | 1 | 121257 | 121257
K/1/3 | Window type W3 overall size 5400mm x 1750mm
K/1/3/1 | in L/G/ floor | Nos. | 12 | 106884 | 1282608
K/1/3/2 | in G/ floor | Nos. | 4 | 106884 | 427536
K/1/3/3 | in 1st floor | Nos. | 8 | 106884 | 855072
K/1/3/4 | in 2nd floor | Nos. | 16 | 106884 | 1710144
K/1/3/5 | in 3rd floor | Nos. | 15 | 106884 | 1603260
K/1/3/6 | in 4th floor | Nos. | 15 | 106884 | 1603260
K/1/3/7 | in 5th floor | Nos. | 15 | 106884 | 1603260
K/1/3/8 | in 6th floor | Nos. | 7 | 106884 | 748188
K/1/3/9 | in 7th floor | Nos. | 7 | 106884 | 748188
K/1/3/10 | in 8th floor | Nos. | 7 | 106884 | 748188
K/1/4 | Window type W4 overall size 3200mm x 1750mm
K/1/4/1 | in G/ floor | Nos. | 1 | 60347 | 60347
K/1/4/2 | in 1st floor | Nos. | 1 | 60347 | 60347
K/1/4/3 | in 2nd floor | Nos. | 1 | 60347 | 60347
K/1/4/4 | in 3rd floor | Nos. | 1 | 60347 | 60347
K/1/4/5 | in 4th floor | Nos. | 1 | 60347 | 60347
K/1/4/6 | in 5th floor | Nos. | 1 | 60347 | 60347
K/1/4/7 | in 6th floor | Nos. | 1 | 60347 | 60347
K/1/4/8 | in 7th floor | Nos. | 1 | 60347 | 60347
K/1/4/9 | in 8th floor | Nos. | 1 | 60347 | 60347
K/1/5 | Window type W5 overall size 2000mm x 1750mm
K/1/5/1 | in L/G/ floor | Nos. | 11 | 37988 | 417868
K/1/5/2 | in G/ floor | Nos. | 29 | 37988 | 1101652
K/1/5/3 | in 1st floor | Nos. | 47 | 37988 | 1785436
K/1/5/4 | in 2nd floor | Nos. | 21 | 37988 | 797748
K/1/5/5 | in 3rd floor | Nos. | 20 | 37988 | 759760
K/1/5/6 | in 4th floor | Nos. | 20 | 37988 | 759760
K/1/5/7 | in 5th floor | Nos. | 19 | 37988 | 721772
K/1/5/8 | in 6th floor | Nos. | 9 | 37988 | 341892
K/1/5/9 | in 7th floor | Nos. | 9 | 37988 | 341892
K/1/6 | Window type W6 overall size 1000mm x 1750mm
K/1/6/1 | in L/G/ floor | Nos. | 11 | 17468 | 192148
K/1/6/2 | in G/ floor | Nos. | 29 | 17468 | 506572
K/1/6/3 | in 1st floor | Nos. | 47 | 17468 | 820996
K/1/6/4 | in 2nd floor | Nos. | 21 | 17468 | 366828
K/1/6/5 | in 3rd floor | Nos. | 20 | 17468 | 349360
K/1/6/6 | in 4th floor | Nos. | 20 | 17468 | 349360
K/1/6/7 | in 5th floor | Nos. | 19 | 17468 | 331892
K/1/6/8 | in 6th floor | Nos. | 9 | 17468 | 157212
K/1/6/9 | in 7th floor | Nos. | 9 | 17468 | 157212
K/1/7 | Window type W7 overall size 1000mm x 1000mm
K/1/7/1 | in L/G/ floor | Nos. | 7 | 11354 | 79478
K/1/7/2 | in G/ floor | Nos. | 36 | 11354 | 408744
K/1/7/3 | in 1st floor | Nos. | 41 | 11354 | 465514
K/1/7/4 | in 2nd floor | Nos. | 9 | 11354 | 102186
K/1/7/5 | in 3rd floor | Nos. | 18 | 11354 | 204372
K/1/7/6 | in 4th floor | Nos. | 19 | 11354 | 215726
K/1/7/7 | in 5th floor | Nos. | 19 | 11354 | 215726
K/1/7/8 | in 6th floor | Nos. | 11 | 11354 | 124894
K/1/7/9 | in 7th floor | Nos. | 11 | 11354 | 124894
K/1/7/10 | in 8th floor | Nos. | 11 | 11354 | 124894
K/1/8 | Window type W8 overall size 6400mm x 1000mm
K/1/8/1 | in L/G/ floor | Nos. | 7 | 77096 | 539672
K/1/9 | Window type W9 overall size 6400mm x 2500mm
K/1/9/1 | in 2nd floor | Nos. | 8 | 98428 | 787424
K/1/10 | Window type W10 overall size 6400mm x 1500mm
K/1/10/1 | in G/ floor | Nos. | 1 | 160783 | 160783
K/1/10/2 | in 1st floor | Nos. | 1 | 160783 | 160783
K/1/10/3 | in 2nd floor | Nos. | 1 | 160783 | 160783
K/1/10/4 | in 3rd floor | Nos. | 1 | 160783 | 160783
K/1/10/5 | in 4th floor | Nos. | 1 | 160783 | 160783
K/1/10/6 | in 5th floor | Nos. | 1 | 160783 | 160783
K/1/10/7 | in 6th floor | Nos. | 1 | 160783 | 160783
K/1/10/8 | in 7th floor | Nos. | 1 | 160783 | 160783
K/1/11 | Window type W11 overall size 6400mm x 1000mm
K/1/11/1 | in L/G/ floor | Nos. | 1 | 55589 | 55589
K/1/11/2 | in Mezz. floor | Nos. | 9 | 55589 | 500301
K/1/11/3 | in G/ floor | Nos. | 3 | 55589 | 166767
K/1/11/4 | in 1st floor | Nos. | 5 | 55589 | 277945
K/1/11/5 | in 2nd floor | Nos. | 8 | 55589 | 444712
K/1/11/6 | in 3rd floor | Nos. | 6 | 55589 | 333534
K/1/11/7 | in 4th floor | Nos. | 6 | 55589 | 333534
K/1/11/8 | in 5th floor | Nos. | 6 | 55589 | 333534
K/1/11/9 | in 6th floor | Nos. | 3 | 55589 | 166767
K/1/11/10 | in 7th floor | Nos. | 3 | 55589 | 166767
DOORS
K/2 | TOUGHEN GLASS PARTITIONS WITH DOORS
Refer Dwg. No: HB/AR/52/T to 59/T
Frame less toughen glass (12mm thick) doors/ Partition shall be as per the drawing. Rate shall include for hinges, brackets, handle, door stop, locking arrangement and any other accessories to completion and working order .
K/2/1 | Partition type, P16 overall size 6400mm x 3900mm , comprising with partition and auto mated sliding door (D1)
K/2/1/1 | in G/ floor | Nos. | 1 | 475273 | 475273
K/2/2 | Partition type, P-18 overall size 6287mm x 3400mm , comprising with partition and 2 Nos: of double sashed swing doors (FD1)
K/2/2/1 | in G/ floor | Nos. | 2 | 491800 | 983600
K/2/2/2 | in 1st floor | Nos. | 2 | 491800 | 983600
K/2/2/3 | in 2nd floor | Nos. | 2 | 491800 | 983600
K/2/2/4 | in 3rd floor | Nos. | 1 | 491800 | 491800
K/2/2/5 | in 4th floor | Nos. | 1 | 491800 | 491800
K/2/2/6 | in 5th floor | Nos. | 1 | 491800 | 491800
K/2/3 | Partition type, P-19 overall size 3310mm x 3400mm , comprising with partition and 1 No: double sashed swing door ( FD1)
K/2/3/1 | in 1st floor | Nos. | 1 | 260685 | 260685
K/2/3/2 | in 2nd floor | Nos. | 2 | 260685 | 521370
K/2/3/3 | in 3rd floor | Nos. | 2 | 260685 | 521370
K/2/3/4 | in 4th floor | Nos. | 2 | 260685 | 521370
K/2/3/5 | in 5th floor | Nos. | 1 | 260685 | 260685
K/2/3/6 | in 6th floor | Nos. | 1 | 260685 | 260685
K/2/3/7 | in 7th floor | Nos. | 1 | 260685 | 260685
K/2/3/8 | in 8th floor | Nos. | 1 | 260685 | 260685
K/2/3 | Partition type, P-17 overall size 6287mm x 3900mm , comprising with partition only
K/2/3/1 | in G/ floor | Nos. | 2 | 414930 | 829860
K/3 | PARTITIONS WITH DOORS
Partition comprise wirh Al. frame, Al. Composit panel, 5mm thick clear glass, sand blast effect film and door (type- ) shall be as per the drawing. Rate shall include for hinges, brackets, handle, door stop, locking arrangement and any other accessories to completion and working order .
K/3/1 | Partition type, P-1 overall size 6225mm x 3600mm , comprising with 2 no.door type, D6'
K/3/1/1 | in G/ floor | Nos. | 1 | 209708 | 209708
K/3/1/2 | in 1st floor | Nos. | 2 | 209708 | 419416
K/3/1/3 | in 2nd floor | Nos. | 2 | 209708 | 419416
K/3/1/4 | in 3rd floor | Nos. | 2 | 209708 | 419416
K/3/1/5 | in 4th floor | Nos. | 2 | 209708 | 419416
K/3/1/6 | in 5th floor | Nos. | 2 | 209708 | 419416
K/3/1/7 | in 6th floor | Nos. | 1 | 209708 | 209708
K/3/1/8 | in 7th floor | Nos. | 1 | 209708 | 209708
K/3/1/9 | in 8th floor | Nos. | 1 | 209708 | 209708
K/3/2 | Partition type, P-2, overall size 6885mm x 2500mm , comprising with 2 no.door type, D8'
K/3/2/1 | in G/ floor | Nos. | 4 | 163403 | 653612
K/3/2/2 | in 1st floor | Nos. | 1 | 163403 | 163403
K/3/3 | Partition type, P-3, overall size 19485mm x 2500mm , comprising with 1 no. of door type, D8' & 1 no. of door type, D10'
K/3/3/1 | in 1st floor | Nos. | 1 | 366370 | 366370
K/3/4 | Partition type, P-4, overall size 5510mm x 2500mm , comprising with 1 no. of door type, D8'
K/3/4/1 | in 1st floor | Nos. | 1 | 120853 | 120853
K/3/5 | Partition type, P-5, overall size 8825mm x 2500mm ,
K/3/5/1 | in 1st floor | Nos. | 1 | 147650 | 147650
K/3/6 | Partition type, P-6, overall size 3775mm x 2500mm ,
K/3/6/1 | in 1st floor | Nos. | 1 | 73037 | 73037
K/3/7 | Partition type, P-7, overall size 6000mm x 2500mm , comprising with 2 no.door type, D8'
K/3/7/1 | in 1st floor | Nos. | 1 | 152608 | 152608
K/3/8 | Partition type, P-8, overall size 3035mm x 2500mm ,
K/3/8/1 | in 1st floor | Nos. | 1 | 105476 | 105476
K/3/9 | Partition type, P-9, overall size 3300mm x 2500mm ,
K/3/9/1 | in 1st floor | Nos. | 1 | 77968 | 77968
K/3/10 | Partition type, P-10, overall size 5510mm x 2500mm , comprising with 5 no. of door type, D8'
K/3/10/1 | in 1st floor | Nos. | 1 | 328986 | 328986
K/3/11 | Partition type, P-11, overall size 4775mm x 2500mm ,
K/3/11/1 | in 1st floor | Nos. | 1 | 94528 | 94528
K/3/12 | Partition type, P-12, overall size 6210mm x 2500mm ,
K/3/12/1 | in 1st floor | Nos. | 1 | 109050 | 109050
K/3/13 | Partition type, P-13, overall size 7235mm x 2500mm , (600mm RCC column in middle)
K/3/13/1 | in 1st floor | Nos. | 1 | 156574 | 156574
K/3/14 | Partition type, P-14, overall size 7235mm x 2500mm ,
K/3/14/1 | in 1st floor | Nos. | 1 | 117347 | 117347
K/3/15 | Partition type, P-15, overall size 6400mm x 2500mm ,
K/3/15/1 | in 1st floor | Nos. | 1 | 106152 | 106152
K/3/16 | Partition type, P-20, overall size 17400mm x 2500mm , (2/600mm RCC column in middle), comprising with 1 no. of door type, D8'
K/3/16/1 | in G/ floor | Nos. | 1 | 314564 | 314564
K/3/17 | Partition type, P-21, overall size 18400mm x 2500mm , comprising with 3 no. of door type, D8'
K/3/17/1 | in G/ floor | Nos. | 1 | 387780 | 387780
K/3/18 | Partition type, P-22, overall size 7000mm x 2500mm ,
K/3/18/1 | in 1st floor | Nos. | 1 | 157932 | 157932
K/3/19 | Partition type, P-23, overall size 3830mm x 2500mm ,
K/3/19/1 | in 1st floor | Nos. | 1 | 88633 | 88633
K/3/20 | Partition type, P-24, overall size 2570mm x 2500mm , comprising with 1 no. of door type, D8'
K/3/20/1 | in G/ floor | Nos. | 1 | 86581 | 86581
K/3/21 | Partition type, P-25, overall size 6375mm x 2500mm ,
K/3/21/1 | in 1st floor | Nos. | 1 | 111469 | 111469
K/3/22 | Partition type, P-26, overall size 5775mm x 2500mm , comprising with 1 no. of door type, D8'
K/3/22/1 | in G/ floor | Nos. | 1 | 125955 | 125955
K/3/23 | Partition type, P-27, overall size 3310mm x 2500mm ,
K/3/23/1 | in 1st floor | Nos. | 1 | 78168 | 78168
K/3/24 | Partition type, P-28, overall size 4120mm x 2500mm ,
K/3/24/1 | in 1st floor | Nos. | 1 | 83540 | 83540
K/3/25 | Partition type, P-29, overall size 3650mm x 2500mm , comprising with 1 no. of door type, D8'
K/3/25/1 | in G/ floor | Nos. | 1 | 108319 | 108319
K/4 | FIRE RATED TIMBER DOORS
Refer Dwg. No: HB/AR/20/T
K/4/1 | Fire rated solid timber (40mm thick sash) doors comprising with 75x100mm timber frame shall be as per the drawing. Rate shall include for hinges, brackets, handle, door stop, other accessories and locking arrangement.
K/4/1 | Type FD, overall size 1000mm x 2100mm
K/4/1/1 | in G/ floor | Nos. | 7 | 152720 | 1069040
K/4/1/2 | in 1st floor |  | 5 | 152893 | 764465
K/4/1/3 | in 2nd floor |  | 6 | 153065 | 918390
K/4/1/4 | in 3rd floor |  | 4 | 153238 | 612952
K/4/1/5 | in 4th floor |  | 4 | 153410 | 613640
K/4/1/6 | in 5th floor |  | 4 | 153583 | 614332
K/4/1/7 | in 6th floor |  | 2 | 153755 | 307510
K/4/1/8 | in 7th floor |  | 2 | 153928 | 307856
K/4/1/9 | in 8th floor |  | 2 | 154100 | 308200
K/4/1/10 | - Ditto- but FD2 overall size, 1500x2100 mm in g/f,2nd F, 3rd F and 4th F | Nos. | 4 | 195845 | 783380 | Addendum01
K/5 | LEAD DOORS
Refer Dwg. No: HB/AR/18/T
K/5/1 | X-Ray froof Lead (Composite door sash comprising with lead sheet as manufactures specifications) doors comprising with Aluminum door frame shall be as per the drawing. Rate shall include for hinges, brackets, handle, door stop, other accessories and locking arrangement.
K/5/1 | Door type D13, overall size 1500mm x 2100mm, double sash swing
K/5/1/1 | in G/ floor | Nos. | 3 | 443900 | 1331700
K/5/1/2 | in 1st floor | Nos. | 1 | 443900 | 443900
K/5/2 | Door type D15, overall size 1000mm x 2100mm, single sash swing
K/5/2/1 | in G/ floor | Nos. | 1 | 358800 | 358800
K/6 | ALUMINUM DOORS
Refer Dwg. No: HB/AR/18/T
K/6/1 | Aluminum door, comprising with sash (Aluminum frame, 5mm thick glass (G) and Al. panel (A)) and Aluminum frame shall be as per the drawing. Rate shall include for hinges, handle, door stop, locking arrangement.
K/6/1 | Door type D4, overall size 1500mm x 2100mm bouble sashed (A&G) swing door
K/6/1/1 | in L/G/ floor | Nos. | 3 | 68841 | 206523
K/6/1/2 | in G/ floor | Nos. | 2 | 68841 | 137682
K/6/1/3 | in 1st floor | Nos. | 2 | 68841 | 137682
K/6/1/4 | in 2nd floor | Nos. | 6 | 68841 | 413046
K/6/1/5 | in 5th floor | Nos. | 3 | 68841 | 206523
K/6/2 | Door type D5, overall size 1500mm x 2100mm bouble sashed (A) swing door
K/6/2/1 | in L/G/ floor | Nos. | 10 | 70299 | 702990
K/6/2/2 | in 1st floor | Nos. | 6 | 70299 | 421794
K/6/2/3 | in 2nd floor | Nos. | 7 | 70299 | 492093
K/6/3 | Door type D6, overall size 1200mm x 2100mm single sashed (A&G) swing door
K/6/3/1 | in L/G/ floor | Nos. | 3 | 42869 | 128607
K/6/3/2 | in G/ floor | Nos. | 25 | 42869 | 1071725
K/6/3/3 | in 1st floor | Nos. | 20 | 42869 | 857380
K/6/3/4 | in 2nd floor | Nos. | 16 | 42869 | 685904
K/6/3/5 | in 3rd floor | Nos. | 10 | 42869 | 428690
K/6/3/6 | in 4th floor | Nos. | 8 | 42869 | 342952
K/6/3/7 | in 5th floor | Nos. | 3 | 42869 | 128607
K/6/3/8 | in 6th floor | Nos. | 4 | 42869 | 171476
K/6/3/9 | in 7th floor | Nos. | 4 | 42869 | 171476
K/6/3/10 | in 8th floor | Nos. | 2 | 42869 | 85738
K/6/4 | Door type D7, overall size 2000mm x 2100mm bouble sashed (G) swing door
K/6/4/1 | in L/G/ floor | Nos. | 3 | 65683 | 197049
K/6/4/2 | in 8th floor | Nos. | 1 | 65683 | 65683
K/6/5 | Door type D8, overall size 1000mm x 2100mm single sashed (A&G) swing door
K/6/5/1 | in L/G/ floor | Nos. | 14 | 35279 | 493906
K/6/5/2 | in Mezz. floor | Nos. | 7 | 35279 | 246953
K/6/5/3 | in G/ floor | Nos. | 16 | 35279 | 564464
K/6/5/4 | in 1st floor | Nos. | 13 | 35279 | 458627
K/6/5/5 | in 2nd floor | Nos. | 18 | 35279 | 635022
K/6/5/6 | in 3rd floor | Nos. | 10 | 35279 | 352790
K/6/5/7 | in 4th floor | Nos. | 14 | 35279 | 493906
K/6/5/8 | in 5th floor | Nos. | 14 | 35279 | 493906
K/6/5/9 | in 6th floor | Nos. | 6 | 35279 | 211674
K/6/5/10 | in 8th floor | Nos. | 5 | 35279 | 176395
K/6/6 | Door type D9, overall size 1000mm x 2100mm single sashed (A) swing door
K/6/6/1 | in L/G/ floor | Nos. | 22 | 39395 | 866690
K/6/6/2 | in Mezz. floor | Nos. | 4 | 39395 | 157580
K/6/6/3 | in G/ floor | Nos. | 23 | 39395 | 906085
K/6/6/4 | in 1st floor | Nos. | 18 | 39395 | 709110
K/6/6/5 | in 2nd floor | Nos. | 53 | 39395 | 2087935
K/6/6/6 | in 3rd floor | Nos. | 16 | 39395 | 630320
K/6/6/7 | in 4th floor | Nos. | 25 | 39395 | 984875
K/6/6/8 | in 5th floor | Nos. | 38 | 39395 | 1497010
K/6/6/9 | in 6th floor | Nos. | 4 | 39395 | 157580
K/6/6/10 | in 7th floor | Nos. | 4 | 39395 | 157580
K/6/6/11 | in 8th floor | Nos. | 6 | 39395 | 236370
K/6/6/12 | Mechine room | Nos. | 2 | 39395 | 78790
K/6/7 | Door type D10, overall size 1500mm x 2100mm Double sashed (G&A) swing door
K/6/7/1 | in L/G/ floor | Nos. | 7 | 64127 | 448889
K/6/7/2 | in G/ floor | Nos. | 10 | 64127 | 641270
K/6/7/3 | in 1st floor | Nos. | 1 | 64127 | 64127
K/6/7/4 | in 2nd floor | Nos. | 1 | 64127 | 64127
K/6/7/5 | in 4th floor | Nos. | 1 | 64127 | 64127
K/6/7/6 | in 5th floor | Nos. | 1 | 64127 | 64127
K/6/8 | Door type D11, overall size 1200mm x 2100mm Double sashed (G&A) swing door
K/6/8/1 | in L/G/ floor | Nos. | 3 | 58255 | 174765
K/6/8/2 | in G/ floor | Nos. | 1 | 58255 | 58255
K/6/8/3 | in 1st floor | Nos. | 4 | 58255 | 233020
K/6/8/4 | in 3rd floor | Nos. | 1 | 58255 | 58255
K/6/8/5 | in 5th floor | Nos. | 1 | 58255 | 58255
K/6/9 | Door type D12, overall size 750mm x 2100mm single sashed (A) swing door
K/6/9/1 | in L/G/ floor | Nos. | 20 | 33472 | 669440
K/6/9/2 | in Mezz. floor | Nos. | 7 | 33472 | 234304
K/6/9/3 | in G/ floor | Nos. | 31 | 33472 | 1037632
K/6/9/4 | in 1st floor | Nos. | 36 | 33472 | 1204992
K/6/9/5 | in 2nd floor | Nos. | 43 | 33472 | 1439296
K/6/9/6 | in 3rd floor | Nos. | 41 | 33472 | 1372352
K/6/9/7 | in 4th floor | Nos. | 37 | 33472 | 1238464
K/6/9/8 | in 5th floor | Nos. | 25 | 33472 | 836800
K/6/9/9 | in 6th floor | Nos. | 14 | 33472 | 468608
K/6/9/10 | in 7th floor | Nos. | 14 | 33472 | 468608
K/6/9/11 | in 8th floor | Nos. | 17 | 33472 | 569024
K/6/10 | Door type D14, overall size 2000mm x 2100mm Double sashed (G&A) swing door
K/6/10/1 | in G/ floor | Nos. | 2 | 73913 | 147826
K/6/10/2 | in 2nd floor | Nos. | 10 | 73913 | 739130
K/6/10/3 | in 3rd floor | Nos. | 2 | 73913 | 147826
K/6/10/4 | in 4th floor | Nos. | 4 | 73913 | 295652
K/6/10/5 | in 5th floor | Nos. | 9 | 73913 | 665217
K/6/11 | Door type D16, overall size 1200mm x 2100mm Single sashed (MP &G) swing door in disable toilet, Rate shall include for stainless steel kick plate
K/6/11/1 | in 1st floor | Nos. | 4 | 50271 | 201084
K/6/11/2 | in 2nd floor | Nos. | 8 | 50271 | 402168
K/6/11/3 | in 3rd floor | Nos. | 12 | 50271 | 603252
K/6/11/4 | in 4th floor | Nos. | 10 | 50271 | 502710
K/6/11/5 | in 5th floor | Nos. | 5 | 50271 | 251355
K/6/11/6 | in 6th floor | Nos. | 4 | 50271 | 201084
K/6/11/7 | in 7th floor | Nos. | 4 | 50271 | 201084
K/6/11/8 | in 8th floor | Nos. | 1 | 50271 | 50271
K/6/12 | Door type D17, overall size 2000mm x 2100mm Double sashed (A) swing door
K/6/12/1 | in 8th floor | Nos. | 11 | 70299 | 773289
K/6/13 | Door type D19, overall size 600mm x 2100mm Double sashed (Aluminum louvers) swing door
K/6/13/1 | in L/G/ floor | Nos. | 5 | 27206 | 136030
K/6/13/2 | in G/ floor | Nos. | 16 | 27206 | 435296
K/6/13/3 | in 1st floor | Nos. | 16 | 27206 | 435296
K/6/13/4 | in 2nd floor | Nos. | 14 | 27206 | 380884
K/6/13/5 | in 3rd floor | Nos. | 15 | 27206 | 408090
K/6/13/6 | in 4th floor | Nos. | 12 | 27206 | 326472
K/6/13/7 | in 5th floor | Nos. | 13 | 27206 | 353678
K/6/13/8 | in 6th floor | Nos. | 7 | 27206 | 190442
K/6/13/9 | in 7th floor | Nos. | 1 | 27206 | 27206
K/6/13/10 | in 8th floor | Nos. | 6 | 27206 | 163236
K/6/13/11 | Machine room | Nos. | 1 | 27206 | 27206
K/7 | ALUMINUM LOUVER PANEL
Refer Dwg. No: HB/AR/60/T
K/7/1 | Aluminum louver panel, ccomprising with louver leaf and aluminum frame shall be as per the drawing. Rate shall include for any accessories to complete.
K/7/1 | Louver panel , hight, 1800mm approximate
K/7/1/1 | in L/G/ floor | m2 | 69 | 13159 | 907971
K/8 | ALUMINUM ROLLER SHUTTERS
Refer Dwg. No: HB/AR/19/T
K/8/1 | Aluminum roller shutter, comprising with roller sash (inter locking aluminum plates) and galvernized steel railing shall be as per the drawing. Rate shall include for railing, handle,hoisting electric moter, door stop, locking arrangement and all accessories to working order.
K/8/1 | Roller shutter type RS2, overall size 4700mm x 4000mm
K/8/1/1 | in L/G/ floor | Nos. | 1 | 196903 | 196903
K/8/2 | Roller shutter type RS4, overall size 3600mm x 4000mm
K/8/2/1 | in L/G/ floor | Nos. | 1 | 153353 | 153353
K/8/3 | Roller shutter type RS5, overall size 1500mm x 4000mm
K/8/3/1 | in L/G/ floor | Nos. | 1 | 88458 | 88458
K/8/4 | - Ditto - but powder coated aluminum Grill roller shutter. type RS- 6, overall size 2500mm x 4400mm
K/8/4/1 | in L/G/ floor | Nos. | 1 | 190429 | 190429
K/9 | Stainless steel roller shutter, comprising with roller sash (inter locking stainless steel plates) and galvernized steel railing shall be as per the drawing. Rate shall include for railing, handle,hoisting electric moter, door stop, locking arrangement and all accessories to working order.
K/9/1 | Roller shutter type RS1, overall size 5400mm x 3900mm
K/9/1/1 | in L/G/ floor | Nos. | 5 | 576610 | 2883050
K/9/1/2 | in G/ floor | Nos. | 2 | 576610 | 1153220
K/9/2 | Roller shutter type RS3, overall size 4500mm x 4400mm
K/9/2/1 | in L/G/ floor | Nos. | 1 | 537984 | 537984
K/10 | Steel Hand Rails
Refer Dwg. No: ENP-HB/AR/R6/01
Following quantities are for G/F to 8th floor
K/10/1 | Supply and fix steel hand rail, Type - 1, fixed to RCC beam (measured separately at miscellaneous work) on half height walls at stair way . Rate shall include for approved marine painting system. All as per the drawing/ approved shop drawing | m | 273 | 3591 | 980343
K/10/2 | - dito- but Type - 3, on walls at balconies | m | 161 | 3591 | 578151
K/10/3 | - dito- but Type - 2, fixed to Concrete pocket (225x225x150mm)at 1.0m interval , embedded to side wall at stair way | m | 69 | 3513 | 242397
K/10/4 | - dito - but hand rail as per Dwg. No: HB/AR/26/T on ramp walls at 1st floor | m | 62 | 9934 | 615908
K/11 | Composite Mezzanine floor
K/11/1 | Supply material, Fabricate, and erect and cast in place Composite Mezzanine floor (steel and concrete) comprising of Primary beams (203x133mm-30kg/m), (305x102-33kg/m),Secondary beams (152x89mmx16kg/m),and column (203,x203x54kg/m) profiled steel sheet deck and any other component to complete the work as shown in the drawing. Rate shall include for painting with two coat of Zink phosphate primer or approved equal ant on exposed steel surfaces.
| The scope of work on the above Item No: K/11/1 shall be carriedout by a specilized sub contractor (Blue Scope LYSAGHT or other supplier approved by consultant)nominated by the client or Consultant. Main contractor shall include an attendance fee (Aproxymately 7% of subcontractor's price). | Note
K/11/1/1 | Mezzanine floor of grid F4 ~ G5 | m2 | 42 | 32902 | 1381884
K/11/1/2 | Mezzanine floor of grid F7 ~ G9 | m2 | 91 | 32902 | 2994082
K/11/1/3 | Mezzanine floor of grid D12 ~ F13 | m2 | 98 | 32902 | 3224396
K/11/1/4 | Mezzanine floor of grid G15 ~ H16 | m2 | 49 | 32902 | 1612198
K/11/1/5 | Mezzanine floor of grid J15 ~ K16 | m2 | 49 | 32902 | 1612198
K/11/1/6 | Mezzanine floor of grid M11 ~ N13 | m2 | 98 | 32902 | 3224396
K/11/2 | Supply material, Fabrication, and fixing steel stair fligt including hand rail to reach Mezzanine floors. Rate shall include for all accessories as per the drawing No:HB/AR/25/T
K/11/2/1 | Stair Case Type - 01 (single flight) | Nr | 4 | 560900 | 2243600
K/11/2/2 | Stair Case Type - 02 (double flight) | Nr | 2 | 521998 | 1043996
K/11/3 | Supply material, Fabrication, and fixing steel spiral stair fligt including hand rail to reach Mechine room roof top. Rate shall include for all accessories | Nr | 1 | Deleted |  | Addendum 02
K/12 | Steel Trusses at Entrance Porch roof
Refer Dwg No: HB/AR/61
K/12/1 | Fabricating and placing Truss at valley, span 7.8 m, with 76mm dia and 50mm dia G.I. pipe including all accessories as per the drawing. Rate shall include for marine paint system, approved by the Engineer. | Nr | 4 | 391100 | 1564400 | Addendom-02
K/12/2 | - ditto - but other Truss, span 5.4 m | Nr | 8 | 377100 | 3016800 | Addendom-02
K/12/3 | Fabricating and placing Bracing unit at front outer edge of roof, span 19.5 m, with 76mm dia. (3 rows) and 50mm dia G.I. pipe, covering both side with Al. composit panel including all accessories as per the drawing. Rate shall include for marring paint system on steel surfaces, approved by the Engineer. | item | 1 |  | 222386 | Addendom-02
K/12/4 | - ditto - but span 11.5 m and 76mm dia (2rows) | item | 1 |  | 264375 | Addendom-02
K/13 | Steel Frame work for Polycarbonate roofs
Refer Drawing: HB/AR/60/T
K/13/1 | Fabricating and erecting steel frame work for poly carbonate roof at 3rd floor, 6th floor and roof slab level, with 100x200mm & 50x50mm box iron, 100mm &75mm dia G.I. pipe including all accessories as per the drawing. Rate shall include for marring paint system, approved by the Engineer.
K/13/1/1 | For frame in 6th floor and roof slab | Nr | 2 | 2720700 | 5441400
K/13/1/2 | For frame in 3rd floor | Nr | 1 | 2250600 | 2250600
K/14 | Canopy
Refer Drawing: HB/AR/62/T
K/14/1 | Supply material, fabricating and fixing Canopy, with aluminum composit panel, H iron & box iron and any other accessories to complete as per the drawing. All steel surfaces shall be painted with Marine paint system.
K/14/1/1 | at G/F | Item | 1 | 912900 | 912900
K/15 | "C" Purlins (Galvanized)
Refer Drawing: HB/AR/61/T
K/15/1 | Supplying & fixing of "C" Purlins, 102 x 51 x 15mm, 1.9mm thk, on steel truss with all the necessary fixing arrangements as per the drawing.
K/15/1/1 | For Zink aluminum sheet roof at entrance porch | m | 225 | 1357 | 305325 | Adden 02
K/16 | Expantion Joint
Refer Drawing: HB/ST/22/T & 42/T
K/16/1 | Supply material, and provide expantion joint between RCC slab and column etc. comprising with 25mm thick soft board, backer rod, polysulphide sealent and any other material to complete as per the drawing
K/16/1/1 | At G/F level, Grid, E11 to E15 | m | 28 | 4209 | 117852
K/16/1/2 | At 1st F/ level, Grid, B11 to E15 and E11 to E15 | m | 49 | 4209 | 206241
K/16/1/3 | At 2nd F/ level, Grid, A11 to D11 and E11 to E15 | m | 36 | 4209 | 151524
K/16/1/4 | At 3rd F/ level, Grid, A11 to D11 and E11 to E15 | m | 56 | 4209 | 235704
| TOTAL CARRIED TO SUMMARY |  |  | Rs | 138018049

## roofing
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
BILL OF QUANTITIES |  | ROOF COVERING AND ROOF PLUMBING
ITEM NO | DESCRIPTION | UNIT | QTY | RATE (RS) | AMOUNT (RS)
P/- | ROOF COVERING / ROOF PLUMBING
Note
Roofing shall consist of Zinc-Aluminum Coloured Bonded profiled high tensile steel complete with all flashings fixings and accessories in strict conforming to British standards 9868:1972 or Indian standards 1252:1975. Thickness of coated sheet shall not be less than 0.47mm. conforming to British standards 9868:1972 or Indian standards
The contractor is required to provide a guarantee for the whole of roof installation against defective materials and defective workmanship for a period of 10 years.
P/1 | Zinc-Aluminum Roof Covering
Roofing shall consist of Zinc-Aluminum Coloured Bonded profiled high tensile steel complete with all flashings fixings and accessories in strict conforming to British standards 9868:1972 or Indian standards 1252:1975. Thickness of coated sheet shall not be less than 0.47mm. conforming to British standards 9868:1972 or Indian standards
P/1/1 | Furnish & install roof covering with 0.47mm thick Zinc-Alum sheet on C purling . C purling measured separately in metal work. | m2 | 270 | 1584 | 427680
P/1/2 | Refer metal work for Trusses, Bracing unit and cladding work. | Note
P/2 | Poly Carbonate sheet Roof Covering
P/2 | Furnish & install Poly Carbonate Roof Covering (curved) as per Dwg. No: HB/AR/60/T, on steel frame work measured separately in Metal work .
P/2/1 | at just above 3rd floor flat roof | m2 | 114 | 8784 | 1001376
P/2/2 | at just above 6th floor flat roof | m2 | 170 | 9281 | 1577770
P/2/3 | at just above 8th floor flat roof | m2 | 170 | 9612 | 1634040
P/3 | Supplying, laying & bedding Zn /Al flashing (to side of RCC wall/beam in Entrance porch roof) with fixing bolt & nut etc. | m | 21 | 1004 | 21084
P/4 | Furnish and install 100x75mm Zn/Al down pipes (0.42mm thick sheet) including all necessary accessories such as, brackets (1.0m C/C) , joints, offsets, bends, shoes etc. Rate shall include for proper connection to rain water gutters/roof slab and surface water drain line As directed by Engineer.
P/4/1 | From RCC gutter box as per drawing (at porch) to pond | m | 18 | 1277 | 22986
P/4/2 | From flat roof (single story Bld.) to Lower G/F | m | 36 | 1277 | 45972
P/4/3 | From 1st floor flat roof to G/F | m | 12 | 1303 | 15636
P/4/4 | From 2nd floor flat roof to G/F | m | 50 | 1329 | 66450
P/4/5 | From 3rd floor slab level to G/F | m | 126 | 1354 | 170604
P/4/6 | From 6th floor slab level to G/F | m | 184 | 1380 | 253920
P/4/7 | From roof slab level to G/F | m | 243 | 1405 | 341415
| TOTAL CARRIED TO SUMMARY |  |  | RS | 5578933

## Elec
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
BILL OF QUANTITIES |  | ELECTRICAL WORKS
ITEM NO | DESCRIPTION | UNIT | Qty | RATE (RS) | AMOUNT (RS)
S | ELECTRICAL WORKS
For the full description of materials and workmanship refer specifications, drawings and preamble notes
ELECTRICAL
PREAMBLE NOTES
EXTENT OF WORK
| The extent of work covered in this Bill of Quantities shall consists of all the items covered under the specifications. |  | note |  |  | note
The extent of work covered in this Bill of Quantities shall consists of all the items covered under the specifications.
a) Provisions of holes, chases….etc.
b) All necessary scaffoldings
c) Contractor's overheads & profits
| d) All tax, levy or duty |  | note |  |  | note
MAIN SERVICE CONNECTION
| It shall be the responsibility of the Contractor to do all the necessary co-ordination work with regards to obtaining of the electrical power connections from the Relevant Authourities . |  | note |  |  | note
WIRING IN GENERAL
| All the wiring work done under this contract shall conform to BS 7671: 1992 - IEE wiring regulations-17th Edition and any other regulations stipulated by the Relevant Authourities. |  | note |  |  | note
| Rate for point wiring shall include for all the conduits, conduit fittings, casings, fixing material, switches, wiring and terminations, holders for light fittings and socket outlets for power points. |  | note |  |  | note
| As a standard of quality for switches and socket outlets, the contractor may use Kevilton, ABB, orange or an equivalent make. |  | note |  |  | note
LIGHT FITTINGS
| The light fittings supplied and installed under this contract shall be in every respect suitable for the intended purpose. |  | note |  |  | note
| Each fitting shall include bulbs, internal wiring, hanging and fixing material and be complete without any additional item/material being required to make it so. |  | note |  |  | note
PANEL BOARDS AND SWITCHGEAR
| The panel boards supplied and installed under this contract shall be complete with all the requires accessories such as neutral bars, earth bars, fixing material……etc. |  | note |  |  | note
EARTHING
| Rates for the earthing system shall include for all the wiring from individual DBs to a common earth bar and from there to the earth pit including construction of the pit, concrete cover…….etc. |  | note |  |  | note
S.1 | Below Ground Floor to 8th Floor
ELECTRICAL INSTALLATIONS FINAL SUB CIRCUIT POINT WIRING
LIGHTING FIXTURES
| All the wiring work done under this contract shall conform to BS 7671: 1992 - IEE wiring regulations-17th Edition and any other regulations stipulated by the Relevant Authourities. |  | note |  |  | note
| Rate for point wiring shall include for all the conduits, conduit fittings, casings, fixing material, switches, wiring and terminations, holders for light fittings and socket outlets for power points. |  | note |  |  | note
| As a standard of quality for switches and socket outlets, the contractor may use Kevilton, ABB, orange or an equivalent make. |  | note |  |  | note
LIGHT FITTINGS
| The light fittings supplied and installed under this contract shall be in every respect suitable for the intended purpose. |  | note |  |  | note
| Each fitting shall include bulbs, internal wiring, and be complete without any additional item/material being required to make it so. |  | note |  |  | note
FINAL SUB CIRCUIT POINT WIRING
Rates for point wiring shall include for all cables, switches(1 way or 2 way as nscessary) Junction boxes, conduits, Pull boxes, clips, earth cables, draw wires, wiring accessories, screws, nails, hardware, fixing and insulating materials, cutting holes. Wire sizes for light points will be 2x1.5mm2 Cu/PVC/PVC 1C Cable+ 2.5mm2 Cu/PVC Earth Cable
K.1.1 | 2x600mm ceiling mounted T5 fluorecent lamp fitting with reflector | nr | 560 | 8840 | 4950400
S.1.2 | 1x600mm ceiling mounted T5 fluorecent lamp fitting with reflector | nr | 1124 | 7436 | 8358064
S.1.3 | 20W CFL downlight fitting | nr | 975 | 6396 | 6236100
S.1.4 | 11W CFL Pendent fitting | nr | 220 | 4680 | 1029600
S.1.5 | 20W CFL wallbracket | nr | 205 | 6240 | 1279200
S.1.6 | 9W downlight fitting | nr | 85 | 7124 | 605540
S.1.7 | 9W nitch light fitting | nr | 51 | 7280 | 371280
S.1.8 | Supply & install 2x2.5mm2 Cu/PVC/PVC cables and 2.5mm2 Cu/PVC Earth with all accessories and wire for 230 V 15A single switch socket outlet. | nr | 217 | 5876 | 1275092
S.1.9 | Supply & install 2x2.5mm2 Cu/PVC/PVC cables and 2.5mm2 Cu/PVC with all accessories and wire for 230 V radial line 13A single switch socket outlet. | nr | 2210 | 6084 | 13445640
S.1. | CEILING FAN
| Supplying all materials for wiring and wiring of 56" Ceiling fan using 2 x 1.5mm2 CU/PVC Cable + 1.5mm2 Cu/PVC earth cable drawn through securety concealed PVC conduits & controlled by switched fan regulator as per the drawings and specifications. | nr | 667 | 3120 | 2081040
| Supply and Install 56" Ceiling fan with switched fan regulator as per the drawings and specifications. | nr | 667 | 8840 | 5896280
EXHAUST FAN
| Supplying all materials for wiring and wiring of Wall mounted fan using 2 x 1.5mm2 CU/PVC Cable + 1.5mm2 Cu/PVC earth cable drawn through securety concealed PVC conduits as per the drawings and specifications. | nr | 25 | 3120 | 78000
| Supply and Install Exhaust fan as per the drawings and specifications. | nr | 25 | 13000 | 325000
S.2 | PANEL BOARDS AND SWITCHGEAR
The panel boards supplied and installed under this contract shall be complete with all the requires accessories such as neutral bars, earth bars, fixing material……etc.
The following may be used as a standard of quality expected in this project.
Enclosures - ' ELSTEEL' or equivalent
MCCBs - 'ABB/TEMBREAK' or equivalent
S.2.1 | BUILDING DB - BDB
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
Shunt Tripping Coil -2nr
ELR-3nr
Core Balance Current Transformer-2nr
Voltmeter with Selector Switch-1nr
Ammeter with Selector Switch-1nr
4 Pole MCCB - 2000A - 3nr (MOTO)
ATS Interlock
3 Pole MCCB - 630A-1nrs
3 Pole MCB - 25A-2nrs
3 Pole MCCB - 800A-2nrs
3 Pole MCB - 63A-1nrs
3 Pole MCB - 40A-1nrs
LED Indicators-3nrs
| MCB Type 15kA ZNO Surge Diverters - 4nrs | nr | 1 | 9100000 | 9100000
Power Analyzer -1nr
1 Set of 3000A TPN & Earth Copper Busbar System
Complete set of cable Glands incommer and outgoing cables
1 No of floor standing metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications.
S.2.2 | LIFT DB
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
1 Set of 600A TPN & Earth Copper Busbar System
3 Pole MCCB - 200A-1nr
ELR with Core Balance Transforemer - 1nr
3 Pole MCB - 63A-4nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 223600 | 223600
S.2.3 | FDB - Below GRN Floor
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
1 Set of 600A TPN & Earth Copper Busbar System
4 Pole MCCB - 400A-1nr
ELR with Core Balance Transforemer - 1nr
3 Pole MCCB - 250A-2nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 324480 | 324480
S.2.3.1 | DB 1
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
1 Set of 400A TPN & Earth Copper Busbar System
4 Pole MCCB - 250A-1nr
ELR With Shunt
3 Pole MCCB - 25A-1nr
3 Pole MCB - 16A-1nr
1 Pole MCB - 16A-18nr
1 Pole MCB - 6A-21nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 312000 | 312000
S.2.3.2 | DB 2
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 250A-1nr
ELR With Shunt
3 Pole MCCB - 125A-1nr
3 Pole MCCB - 40A-1nr
1 Pole MCB - 16A-18nr
1 Pole MCB - 6A-21nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 239200 | 239200
S.2.4 | FDB AC
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 40A-1nr
4 Pole 40A RCCB - 1 nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 98800 | 98800
S.2.5 | FDB - MEZZ FLOOR
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 25A-1nr
4 Pole RCCB - 25A - 1nr
3 Pole MCB - 16A-2nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 104000 | 104000
S.2.5.1 | DB1
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 16A-1nr
4 Pole RCCB - 25A-1nr
1 Pole MCB - 16A-6nr
1 Pole MCB - 6A-9nr
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 80080 | 80080
S.2.5.2 | DB 2
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 16A-1nr
4 Pole RCCB 25A - 1nr
1 Pole MCB - 16A-6nr
1 Pole MCB - 6A-9nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 81640 | 81640
S.2.6 | FDB AC
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 16A-1nr
4 Pole RCCB - 25A-1nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 83200 | 83200
S.2.7 | FDB (GROUND FLOOR)
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
4 Pole MCCB - 100A-1nr
4 Pole RCCB - 100A - 1nr
3 Pole MCB - 40A-3nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 156000 | 156000 |  | 56734236
S.2.7.1 | DB1
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 40A-1nr
4 Pole RCCB - 40A-1nr
1 Pole MCB - 16A-16nr
1 Pole MCB - 6A-9nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 88400 | 88400
S.2.7.2 | DB 2
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 40A-1nr
4 Pole RCCB - 40A-1nr
1 Pole MCB - 16A-16nr
1 Pole MCB - 6A-9nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 88400 | 88400
S.2.7.3 | DB 3
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 40A-1nr
4 Pole RCCB - 40A-1nr
1 Pole MCB - 16A-16nr
1 Pole MCB - 6A-9nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 88400 | 88400
S.2.8 | FDB AC
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 40A-1nr
4 Pole RCCB - 40A-1nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 78000 | 78000
S.2.9 | FDB FIRST FLOOR
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
4 Pole MCCB - 160A-1nr
ELR With Shunt
3 Pole MCCB - 100A-3nr
3 Pole MCB - 25A-1nr
3 Pole MCB - 40A-1nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 195000 | 195000
S.2.9.1 | DB 1
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
4 Pole MCB - 100A-1nr
ELR with Core Balance Transforemer - 1nr
3 Pole MCB - 16A-3nr
3 Pole MCB - 10A-8nr
1 Pole MCB - 16A-25nr
1 Pole MCB - 6A-15nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 192400 | 192400
S.2.9.2 | DB 2
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 25A-1nr
4 Pole RCCB - 25A-1nr
1 Pole MCB - 16A-10nr
1 Pole MCB - 6A-10nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 93600 | 93600
S.2.9.3 | DB 3
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 40A-1nr
4 Pole RCCB - 40A-1nr
1 Pole MCB - 16A-16nr
1 Pole MCB - 6A-19nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 104000 | 104000
S.2.10 | FDBAC
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 63A-1nr
4 Pole RCCB - 63A-1nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 73320 | 73320
S.2.11 | FDB SECOND FLOOR
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
4 Pole MCCB - 160A-1nr
ELR with Core Balance Transforemer - 1nr
3 Pole MCB - 100A-1nr
3 Pole MCB - 40A-1nr
3 Pole MCB - 25A-2nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 2 | 223600 | 447200
S.2.11.1 | DB 1
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
4 Pole MCCB - 100A-1nr
ELR with Core Balance Transforemer - 1nr
3 Pole MCB - 16A-8nr
3 Pole MCB - 10A-4nr
1 Pole MCB - 16A-15nr
1 Pole MCB - 10A-15nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 228800 | 228800
S.2.11.2 | DB2
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 40A-1nr
4 Pole RCCB - 40A-1nr
3 Pole MCB - 16A-3nr
3 Pole MCB - 10A-4nr
1 Pole MCB - 16A-15nr
1 Pole MCB - 6A- 8nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 4 | 145600 | 582400
S.2.11.3 | DB 3
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 25A-1nr
4 Pole RCCB - 25A - 1nr
1 Pole MCB - 16A-16nr
1 Pole MCB - 6A-15nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 93600 | 93600
S.2.11.4 | DB 4
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 25A-1nr
4 Pole RCCB - 25A-1nr
1 Pole MCB - 16A-16nr
1 Pole MCB - 6A-15nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 93600 | 93600
S.2.12 | FDB AC
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 100A-1nr
ELR with Core Balance Transforemer - 1nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 166400 | 166400
S.2.13 | FDB THIRD FLOOR
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 63A-1nr
4 Pole RCCB - 63A-1nr
3 Pole MCB - 63A-2nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 3 | 87880 | 263640
S.2.13.1 | DB 1
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 63A-1nr
4 Pole RCCB - 63A-1nr
1 Pole MCB - 16A-18nr
1 Pole MCB - 6A-15nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 109200 | 109200
S.2.13.2 | DB 2
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 63A-1nr
4 Pole RCCB - 63A-1nr
1 Pole MCB - 16A-18nr
1 Pole MCB - 6A-15nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 109200 | 109200
S.2.14 | FDB FORTH FLOOR
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
4 Pole MCCB - 100A-1nr
ELR with Core Balance Transforemer - 1nr
3 Pole MCB - 32A-3nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 187200 | 187200
S.2.14.1 | DB 1
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 32A-1nr
4 Pole RCCB - 40A-1nr
1 Pole MCB - 16A-12nr
1 Pole MCB - 10A-8nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 101400 | 101400
S.2.14.2 | DB2
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 32A-1nr
4 Pole RCCB - 40A-1nr
1 Pole MCB - 16A-15nr
1 Pole MCB - 10A-10nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 104000 | 104000
S.2.14.3 | DB 3
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 32A-1nr
4 Pole RCCB - 40A-1nr
1 Pole MCB - 16A-15nr
1 Pole MCB - 10A-10nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 104000 | 104000
S.2.15 | FDB AC
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 63A-1nr
4 Pole RCCB - 63A-1nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 75400 | 75400
S.2.16 | FDB FIFTH FLOOR
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
4 Pole MCCB - 100A-1nr
ELR with Core Balance Transforemer - 1nr
3 Pole MCB - 32A-3nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 187200 | 187200
S.2.16.1 | DB 1
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 32A-1nr
4 Pole RCCB - 40A-1nr
1 Pole MCB - 16A-12nr
1 Pole MCB - 10A-8nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 114400 | 114400
S.2.16.2 | DB2
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 32A-1nr
4 Pole RCCB - 40A-1nr
1 Pole MCB - 16A-15nr
1 Pole MCB - 10A-10nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 104000 | 104000
S.2.16.3 | DB 3
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 32A-1nr
4 Pole RCCB - 40A-1nr
1 Pole MCB - 16A-15nr
1 Pole MCB - 10A-10nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 104000 | 104000
S.2.17 | FDB AC
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 125A-1nr
4 Pole RCCB - 125A-1nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 101400 | 101400
S.2.18 | FDB SIXTH FLOOR
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 63A-1nr
4 Pole RCCB - 63A-1nr
3 Pole MCB - 63A-1nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 83200 | 83200
S.2.18.1 | DB 1
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 63A-1nr
4 Pole RCCB - 63A-1nr
1 Pole MCB - 16A-10nr
1 Pole MCB - 10A-6nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 72800 | 72800
S.2.19 | FDB SEVENTH FLOOR
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 40A-1nr
4 Pole RCCB - 40A-1nr
3 Pole MCB - 40A-1nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 78000 | 78000
S.2.19.1 | DB 1
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 40A-1nr
4 Pole RCCB - 40A-1nr
1 Pole MCB - 16A-10nr
1 Pole MCB - 10A-6nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 78000 | 78000
S.2.20 | FDB EIGHTH FLOOR
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 40A-1nr
4 Pole RCCB - 40A-1nr
3 Pole MCB - 20A-2nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 80600 | 80600
S.2.20.1 | DB 1
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 20A-1nr
4 Pole RCCB - 25A-1nr
1 Pole MCB - 16A-6nr
1 Pole MCB - 10A-4nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 75400 | 75400
S.2.20.2 | DB2
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCCB - 20A-1nr
4 Pole RCCB - 25A-1nr
1 Pole MCB - 16A-6nr
1 Pole MCB - 10A-4nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 75400 | 75400
S.2.21 | FDB AC
To supply and install Metal enclosed Distribution Board including following accessories as per the drawings & specifications.
LED Indicators-3nrs
3 Pole MCB - 63A-1nr
4 Pole RCCB - 63A-1nr
Complete set of cable Glands incommer and outgoing cables
| 1 No of wall mounted metal enclosed distribution board (surface finished with Epoxy polyester base powder spray in bage color) with neutral link completed with Earth bar & mounting accessories, DIN rail type as per IEE Specifications. |  | 1 | 75400 | 75400
S.3 | MAIN CABLING
S.3.1 | Supply Laying & termination of 8x4Co 400 mm2 CU/XLPE/PVC + 4x400mm2 PVC/Cu Earth Cable from MDB to Main Building | m | 10 | 280800 | 2808000
S.3.2 | Supply Laying & termination of 8x4Co 400 mm2 CU/XLPE/PVC + 4x400mm2 PVC/Cu Earth Cable from Main Building to ATS | m | 10 | 280800 | 2808000
S.3.3 | Supply Laying & termination of 8x4Co 400 mm2 CU/XLPE/PVC + 4x400mm2 PVC/Cu Earth Cable from GEN to ATS | m | 15 | 280800 | 4212000
S.3.4 | Supply Laying & termination of 8x4Co 400 mm2 CU/XLPE/PVC + 4x400mm2 PVC/Cu Earth Cable from ATS to BDB-Main Building | m | 10 | 280800 | 2808000
S.4 | SUB MAIN CABLING
BDB to Bus Riser 1
S.4.1 | Supply Laying & termination of 5X4C 400 mm2 CU/XLPE/PVC armoured + 3X400mm2 PVC/Cu Earth Cable from BDB to Bus Riser 1 | m | 70 | 187200 | 13104000
BDB to Bus Riser 2
S.4.2 | Supply Laying & termination of 5X4C 400 mm2 CU/XLPE/PVC armoured + 3X400mm2 PVC/Cu Earth Cable from BDB to Bus Riser 2 | m | 70 | 187200 | 13104000
BDB to FDB(Below Gnd Floor)
S.4.3 | Supply Laying & termination of 2X4C 300 mm2 CU/XLPE/PVC armoured + 300mm2 PVC/Cu Earth Cable from BDB to FDB | m | 10 | 78000 | 780000
BDB to FDB(Mezzaning)
S.4.4 | Supply Laying & termination of 4C 6mm2 CU/XLPE/PVC + 6mm2 PVC/Cu Earth Cable from BDB to FDB | m | 10 | 2574 | 25740
BDB to AC-BG &MEZ
S.4.5 | Supply Laying & termination of 4C 4mm2 CU/XLPE/PVC + 4mm2 PVC/Cu Earth Cable from BDB to Street DB | m | 4 | 2080 | 8320
BDB to Street DB
S.4.6 | Supply Laying & termination of 4C 10mm2 CU/XLPE/PVC + 10mm2 PVC/Cu Earth Cable from BDB to AC | m | 12 | 5408 | 64896
Bus Riser 1 to FDB-GF
S.4.7 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 1 to FDB | m | 6 | 7540 | 45240
Bus Riser 1 to FDBAC-GF
S.4.8 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 1 to FDBAC | m | 6 | 7540 | 45240
Bus Riser 1 to FDB-2nd FL
S.4.9 | Supply Laying & termination of of 4C 50 mm2 CU/XLPE/PVC + 25 mm2 PVC/Cu Earth Cable from Bus Riser 1 to 2nd FDB | m | 6 | 11388 | 68328
Bus Riser 1 to FDB-4th FL
S.4.10 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 1 to 4th FDB | m | 6 | 7540 | 45240
Bus Riser 1 to FDBAC-4th FL
S.4.11 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 1 to 4th FDBAC | m | 6 | 7540 | 45240
Bus Riser 1 to FDB-6th FL
S.4.12 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 1 to 4th FDB | m | 6 | 7540 | 45240
Bus Riser 1 to FDB-8th FL
S.4.13 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 1 to 4th FDB | m | 6 | 7540 | 45240
Bus Riser 1 to FDBAC-8th FL
S.4.14 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 1 to 4th FDBAC | m | 6 | 7540 | 45240
Bus Riser 1 to LIFT 1
S.4.15 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 1 to LIFT 1 | m | 6 | 7540 | 45240
Bus Riser 1 to LIFT 2
S.4.16 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 1 to LIFT 2 | m | 6 | 7540 | 45240
Bus Riser 2 to FDB-1st FL
S.4.17 | Supply Laying & termination of of 4C 50 mm2 CU/XLPE/PVC + 25 mm2 PVC/Cu Earth Cable from Bus Riser 2 to FDB | m | 6 | 11388 | 68328
Bus Riser 2 to FDBAC-1st FL
S.4.18 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 2 to FDBAC | m | 6 | 7540 | 45240
Bus Riser 2 to FDBAC-2nd FL
S.4.19 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 2 to FDBAC | m | 6 | 7540 | 45240
Bus Riser 2 to FDB-3rd FL
S.4.20 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 2 to FDB | m | 6 | 7540 | 45240
Bus Riser 2 to FDB-5th FL
S.4.21 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 2 to FDB | m | 6 | 7540 | 45240
Bus Riser 2 to FDBAC-5th FL
S.4.22 | Supply Laying & termination of of 4C 50 mm2 CU/XLPE/PVC + 25 mm2 PVC/Cu Earth Cable from Bus Riser 2 to FDBAC | m | 6 | 11388 | 68328
Bus Riser 2 to FDB-7th FL
S.4.23 | Supply Laying & termination of of 4C 16 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 2 to FDB | m | 6 | 5980 | 35880
Bus Riser 2 to LIFT 3
S.4.24 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 2 to LIFT 3 | m | 6 | 7540 | 45240
Bus Riser 2 to LIFT 4
S.4.25 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from Bus Riser 2 to LIFT 4 | m | 6 | 7540 | 45240
FDB-BGF to DB1
S.4.26 | Supply Laying & termination of of 4C 150 mm2 CU/XLPE/PVC + 95 mm2 PVC/Cu Earth Cable from FDB-BGF to DB1 | m | 35 | 30004 | 1050140
FDB-BGF to DB2
S.4.27 | Supply Laying & termination of of 4C 240 mm2 CU/XLPE/PVC + 120 mm2 PVC/Cu Earth Cable from FDB-BGF to DB2 | m | 60 | 41392 | 2483520
FDB-MEZ to DB1
S.4.28 | Supply Laying & termination of of 4C 16 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-MEZ to DB1 | m | 60 | 5980 | 358800
FDB-MEZ to DB2
S.4.29 | Supply Laying & termination of of 4C 16 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-MEZ to DB2 | m | 60 | 5980 | 358800
FDB-GF to DB1
S.4.30 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-GF to DB1 | m | 42 | 7540 | 316680
FDB-GF to DB2
S.4.31 | Supply Laying & termination of of 4C 35 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-GF to DB2 | m | 52 | 8164 | 424528
FDB-GF to DB3
S.4.32 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-GF to DB3 | m | 28 | 7540 | 211120
FDB-1st FL to DB1
S.4.33 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-1st FL to DB1 | m | 15 | 7250 | 108750
FDB-1st FL to DB2
S.4.34 | Supply Laying & termination of of 4C 95 mm2 CU/XLPE/PVC + 50 mm2 PVC/Cu Earth Cable from FDB-1st FL to DB2 | m | 55 | 20436 | 1123980
FDB-1st FL to DB3
S.4.35 | Supply Laying & termination of of 4C 150 mm2 CU/XLPE/PVC + 95 mm2 PVC/Cu Earth Cable from FDB-1st FL to DB3 | m | 85 | 30004 | 2550340
FDB-2nd FL to DB1
S.4.36 | Supply Laying & termination of of 4C 70 mm2 CU/XLPE/PVC + 35 mm2 PVC/Cu Earth Cable from FDB-2nd FL to DB1 | m | 40 | 14872 | 594880
FDB-2nd FL to DB2
S.4.37 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-2nd FL to DB2 | m | 37 | 7540 | 278980
FDB-2nd FL to DB3
S.4.38 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-2nd FL to DB3 | m | 45 | 7540 | 339300
FDB-2nd FL to DB4
S.4.39 | Supply Laying & termination of of 4C 10 mm2 CU/XLPE/PVC + 10 mm2 PVC/Cu Earth Cable from FDB-2nd FL to DB4 | m | 5 | 5408 | 27040
FDB-3rd FL to DB1
S.4.40 | Supply Laying & termination of of 4C 16 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-3rd FL to DB1 | m | 11 | 5980 | 65780
FDB-3rd FL to DB2
S.4.41 | Supply Laying & termination of of 4C 50 mm2 CU/XLPE/PVC + 25 mm2 PVC/Cu Earth Cable from FDB-3rd FL to DB2 | m | 48 | 11388 | 546624
FDB-4th FL to DB1
S.4.42 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-4th FL to DB1 | m | 34 | 7540 | 256360
FDB-4th FL to DB2
S.4.43 | Supply Laying & termination of of 4C 10 mm2 CU/XLPE/PVC + 10 mm2 PVC/Cu Earth Cable from FDB-4th FL to DB2 | m | 15 | 5408 | 81120
FDB-4th FL to DB3
S.4.44 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-4th FL to DB3 | m | 45 | 7540 | 339300
FDB-5th FL to DB1
S.4.45 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-5th FL to DB1 | m | 49 | 7540 | 369460
FDB-5th FL to DB2
S.4.46 | Supply Laying & termination of of 4C 25 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from FDB-5th FL to DB2 | m | 43 | 7540 | 324220
FDB-5th FL to DB3
S.4.47 | Supply Laying & termination of of 4C 10 mm2 CU/XLPE/PVC + 10 mm2 PVC/Cu Earth Cable from FDB-5th FL to DB3 | m | 15 | 5408 | 81120
FDB-6th FL to DB1
S.4.48 | Supply Laying & termination of of 4C 10 mm2 CU/XLPE/PVC + 10 mm2 PVC/Cu Earth Cable from FDB-6th FL to DB1 | m | 5 | 5408 | 27040
FDB-7th FL to DB1
S.4.49 | Supply Laying & termination of of 4C 10 mm2 CU/XLPE/PVC + 10 mm2 PVC/Cu Earth Cable from FDB-7th FL to DB1 | m | 5 | 5408 | 27040
FDB-8th FL to DB1
S.4.50 | Supply Laying & termination of of 4C 10 mm2 CU/XLPE/PVC + 10 mm2 PVC/Cu Earth Cable from FDB-8th FL to DB1 | m | 5 | 5408 | 27040
FDB-8th FL to DB2
S.4.51 | Supply Laying & termination of of 4C 10 mm2 CU/XLPE/PVC + 10 mm2 PVC/Cu Earth Cable from FDB-8th FL to DB2 | m | 23 | 5408 | 124384
AC-BG & MEZ
S.4.52 | Supply Laying & termination of of 4C 35 mm2 CU/XLPE/PVC + 16 mm2 PVC/Cu Earth Cable from AC-BG & MEZ to BG | m | 65 | 8164 | 530660
AC-BG & MEZ
S.4.53 | Supply Laying & termination of of 4C 10 mm2 CU/XLPE/PVC + 10 mm2 PVC/Cu Earth Cable from AC-BG & MEZ to MEZ | m | 50 | 5408 | 270400
S.5 | UPS
| Supply and Install 100kVA online UPS with minimum two hour backup |  |  | 14481100 | 14481100
S.5.1 | Rates for the earthing system according to IEEE regulation and shall include for all the wiring from individual DBs to a common earth bar and from there to the earth pit including construction of the pit, concrete cover…….etc. |  |  | 104000 | 104000
S.6 | Supply and Install 800 kVA Generator set as per the specification (Refer specifications) |  |  | 20800000 | 20800000
S.7 | TELEPHONE OUTLETS
S.7.1 | Supply and installation of EPABX of 600 Extentions and 20 incoming lines in Telephone Excahnge room(shown in Dwg No; HB/AR/04/T) as per specifications | nr | 1 | 3120000 | 3120000
S.7.2 | Supply and installtion of Main Distribution Frame of 600 Extentions and Provitions for 30 incoming lines with condutes trunking and all necessary accessories for incoming and extentions | nr | 1 | 187200 | 187200
S.7.3 | Supply and installtion of Sub Distribution Frame each with 100 Extentions with condutes trunking and all necessary accessories for incoming and extentions from Ground floor to 8th floor | nrs | 8 | 52000 | 416000
S.7.4 | Wiring of telephone socket outlet using 0.5mm Single pair telephone cable through securely concealed PVC conduits from the Ground floor telephone switching equipment point at the floor sub Distribution Frame as per the drawings and specifications | nr | 530 | 4680 | 2480400
S.7.5 | Supply and install the operators console | nr | 1 | 208000 | 208000
S.7.6 | Supply of analog phones | nr | 409 | 3640 | 1488760 | Addendum01
S.7.7 | Supply of analog Display Phones with CLI | nr | 4 | 5720 | 22880
S.7.8 | Surge Protection at incoming lines only | nr | 20 | 31200 | 624000
S.8 | NETWORK
Contractor is accepted to submit a shop drawings for net work wiring on cable tray together with fixing detail and obtaining prior approval of the Engineer
S.8.1 | Number of network outlets | nr | 151 | 4680 | 706680 | Addendum01
S.8.2 | 48 Port Layer 2 Switch | nr | 4 | 166400 | 665600
S.8.3 | ADSL Router (10 Mbps Compatible) | nr | 1 | 10400 | 10400
S.8.4 | Ground Floor Switch (24 ports) |  | 1 | 93600 | 93600
S.8.5 | First Floor Switch (24 ports) |  | 1 | 93600 | 93600
S.8.6 | Second Floor Switch (24 ports) |  | 1 | 93600 | 93600
S.8.7 | Third Floor Switch (18 ports) |  | 1 | 78000 | 78000
S.8.8 | Fourth Floor Switch (24 ports) |  | 1 | 93600 | 93600
S.8.9 | Fifth Floor Switch (24 ports) |  | 1 | 93600 | 93600
S.8.10 | Sixth Floor Swithch (24 port) |  | 1 | 93600 | 93600
S.8.11 | Seventh Floor Swithch (24 port) |  | 1 | 93600 | 93600
S.8.12 | Eighth Floor Switch (24 port) |  | 1 | 93600 | 93600
S.8.13 | B/G/N-Wireless Access points |  | 12 | 20800 | 249600
S.8.14 | Supply and wiring of all network lines with shield twised pair cat 5e cable |  | 77 | 5720 | 440440
S.9 | Fire Alarm System
S.9.1 | Supply and install, Fire Alarm Control System to cater 15 Zones in Communication room (shown in Dwg No; HB/AR/04/T) | nr | 1 | 520000 | 520000
S.9.2 | Supply and installtion of adresible manual call points with wiring in conduit trunking etc with fire retarded cable | nr | 116 | 37960 | 4403360 | Addendum01
S.9.3 | Supply and installation of addresible smoke detectors in generator room and cable duct and basement with al wiring | nrs | 5 | 46540 | 232700
S.9.4 | Supply and wiring addresible heat detector in cooking area with all wiring | nr | 2 | 46540 | 93080
S.9.5 | Supply and install the fire alarm sounders | nr | 8 | 41600 | 332800
S.9.6 | Supply and Installation of Repeater alarm unit with acceptance facility in fire control room | nr | 1 | 312000 | 312000
S.10 | Public Address System
S.10.1 | Supply and install, Amplifire and Mixing Pre Amplifire system with Microphone Cassate recorder and FM tuner with antna etc. for the PA system | nr | 1 | 520000 | 520000
K.10.2 | Supply and install ceiling type speakers in the coridors as shown in the drawing flush mounted or surface mounted as shown | nr | 157 | 4160 | 653120 | Addendum01
S.11 | Rates for the earthing system according to IEEE regulation and shall include for all the wiring from individual DBs to a common earth bar and from there to the earth pit including construction of the pit, concrete cover…….etc. | Item |  | 104000 | 104000
S.11a | Allow lump sum for testing & commissing of the total system to the entire satisfaction of the engineer & submition of commissioning report in triplicate | LS |  |  | 100000 | Addendum01
S.12 | Provisional sum for providing lighting protection system | Item |  | P.S. | 3250000
| TOTAL CARRIED TO SUMMARY |  |  |  | 172924342

## Finishes
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
BILL OF QUANTITIES |  | FINISHES
ITEM NO | DESCRIPTION | UNIT | QTY. | RATE (RS) | AMOUNT (RS)
T/- | WALL/FLOOR/ CEILING FINISHES
T/1 | Floor Tilling
T/1/1 | 300mm x 600mm polished porcelain floor tiles paving to an approved pattern including 1:3 cement and sand on 20mm thick screed bed and point with coloured cement to match and forming neat uniform joint between tiles with removable tape joint. Rate shall include for forming arises edges and cutting tiles into required sizes and shape at arises and where necessary and cleaning on completion. (Prime cost for 300x600mm tile shall be Rs 350.00 to 375.00) | [5 empty] | 66542865.3846
T/1/1/1 | in L/G/ floor | m2 | 147 | 3578 | 525966
T/1/1/2 | in G/ floor | m2 | 1897 | 3578 | 6787466
T/1/1/3 | in 1st floor | m2 | 946 | 3650 | 3452900
T1/2 | - ditto- but 600mm x 600mm polished finished porcelain floor tile (Rustic tile) in open areas. (Prime cost for 600x600mm tile shall be Rs 800.00 to 825.00)
T/2/1 | in 2nd floor | m2 | 807 | 4123 | 3327261
T/2/2 | in 3rd floor | m2 | 720 | 4203 | 3026160
T1/3 | - ditto- but 600mm x 300mm mat finished porcelain floor tile (Rustic tile) in open areas. (Prime cost for 600x300mm tile shall be Rs 400.00 to 425.00)
T1/3/1 | in L/G/ floor | m2 | 950 | 3961 | 3762950
T1/3/2 | in Mezz. floor | m2 | 390 | 3961 | 1544790
T1/3/3 | in G/ floor | m2 | 1302 | 3961 | 5157222
T1/3/4 | in 1st floor | m2 | 1333 | 4040 | 5385320
T1/3/5 | in 2nd floor | m2 | 933 | 4119 | 3843027
T1/3/6 | in 3rd floor | m2 | 884 | 4199 | 3711916
T1/3/7 | in 4th floor | m2 | 992 | 4278 | 4243776
T1/3/8 | in 5th floor | m2 | 657 | 4357 | 2862549
T1/3/9 | in 6th floor | m2 | 380 | 4436 | 1685680
T1/3/10 | in 7th floor | m2 | 380 | 4516 | 1716080
T1/3/11 | in 8th floor | m2 | 595 | 4595 | 2734025
T1/3/12 | In main stair case L/GF to 8th floor, step tile shall be with chamfer edge, (Area shall be measured including skirting) | m2 | 334 | 5181 | 1730454
T1/3a | - ditto- but 600mm x 300mm mat finished Ceramic floor tile . (Prime cost for 600x300mm tile shall be Rs 300.00 to 310.00)
T1/3a/1 | in G/ floor and 1st floor | m2 | 2200 | 3165 | 6963000
T1/4 | - ditto- but 600mm x 600mm mat finished porcelain floor tile (Rustic tile) in open areas. (Prime cost for 600x600mm tile shall be Rs 850.00 to 900.00)
T1/4/1 | in L/G/ floor | m2 | 427 | 4206 | 1795962
T1/4/2 | in G/ floor | m2 | 648 | 4206 | 2725488
T1/4/3 | in 1st floor | m2 | 24 | 4290 | 102960
T1/4/4 | in 2nd floor | m2 | 24 | 4374 | 104976
T1/4/5 | in 3rd floor | m2 | 24 | 4458 | 106992
T1/4/6 | in 4th floor | m2 | 768 | 4542 | 3488256
T1/4/7 | in 5th floor | m2 | 670 | 4627 | 3100090
T1/4/8 | in 6th floor | m2 | 530 | 4711 | 2496830
T1/4/9 | in 7th floor | m2 | 530 | 4795 | 2541350
T1/4/10 | in 8th floor | m2 | 257 | 4879 | 1253903
T1/5 | - ditto- but 400mm x 400mm non skipped porcelain floor tile in toilet (Prime cost for 400x400mm tile shall be Rs 375.00 to 400.00) |  |  |  |  | Addendum01
T1/5/1 | in L/G/ floor | m2 | 89 | 4123 | 366947
T1/5/2 | in Mezz. floor | m2 | 10 | 4123 | 41230
T1/5/3 | in G/ floor | m2 | 79 | 4123 | 325717
T1/5/4 | in 1st floor | m2 | 161 | 4205 | 677005
T1/5/5 | in 2nd floor | m2 | 132 | 4288 | 566016
T1/5/6 | in 3rd floor | m2 | 233 | 4370 | 1018210
T1/5/7 | in 4th floor | m2 | 396 | 4453 | 1763388
T1/5/8 | in 5th floor | m2 | 103 | 4535 | 467105
T1/5/9 | in 6th floor | m2 | 84 | 4618 | 387912
T1/5/10 | in 7th floor | m2 | 89 | 4700 | 418300
T1/5/11 | in 8th floor | m2 | 62 | 4783 | 296546
T1/6 | Machine floated neat Cement rendering floor treated with using floor hardener and machine cut to smooth surface finish including 100mm high skirting (Concrete slab measured separately in Concrete item) |  |  |  |  | Addendum01
T1/6/1 | in L/G/ floor | m2 | 980 | 4161 | 4077780
T1/6/2 | in Ramp G/F to 1st floor | m2 | 115 | 4161 | 478515
T1/6/3 | in Entrance porch and ramp | m2 | 418 | 4161 | 1739298
T1/7 | Supply and fixing "Vinyl flooring" as per manufactures specification to engineers approval . Rate shall include for self leveling floor finish , expansion bolt, edge trim, any other accessories and provisions for services line, etc. and 100mm high skirting |  |  |  |  | Addendum01
T1/7/1 | in G/ floor | m2 | 1799 | 4268 | 7678132
T1/7/2 | in 1st floor | m2 | 298 | 4353 | 1297194
T1/7/3 | in 2nd floor | m2 | 1084 | 4439 | 4811876
T1/7/4 | in 4th floor | m2 | 353 | 4609 | 1626977
T1/7/5 | in 5th floor | m2 | 854 | 4695 | 4009530
T1/8 | - ditto- but "Vinyl flooring (ANTI STATIC) " Type
T1/8/1 | in G/ floor | m2 | 203 | 5510 | 1118530
T1/8/2 | in 2nd floor | m2 | 163 | 5730 | 933990
T1/8/3 | in 4th floor | m2 | 4 | 5950 | 23800
T1/8/4 | in 5th floor | m2 | 42 | 6061 | 254562
T1/9 | 15 mm thick Ordinary rendering in cement and sand 1:3 , finished smooth floting in passages
T1/9/1 | in G/ floor | m2 | 12 | 516 | 6192
T1/9/2 | in 1st floor | m2 | 27 | 526 | 14202
T1/9/3 | in 2nd floor | m2 | 32 | 537 | 17184
T1/9/4 | in 3rd floor | m2 | 48 | 547 | 26256
T1/9/5 | in 4th floor | m2 | 50 | 557 | 27850
T1/9/6 | in 5th floor | m2 | 17 | 568 | 9656
T1/9/7 | in 6th floor | m2 | 14 | 578 | 8092
T1/9/8 | in 7th floor | m2 | 14 | 588 | 8232
T1/9/9 | in 8th floor | m2 | 16 | 599 | 9584
T1/10 | - ditto - in fire stair ways, edges of steps shall be rough finish (Area shall be measured including skirting)
T1/10/1 | in L/G/F to 8th floor, | m2 | 498.389 | 614 | 306010.846
T2 | Internal Plaster
T2/6 | Render 15mm thick cement and sand (1:5) and finish smooth with neat finish (Internally) in surfaces of brick masonry and RCC column
T2/6/1 | in L/G/ floor | m2 | 8577 | 639 | 5480703
T2/6/2 | in Mezz. floor | m2 | 346 | 639 | 221094
T2/6/3 | in G/ floor | m2 | 8114 | 639 | 5184846
T2/6/4 | in 1st floor | m2 | 4750 | 652 | 3097000
T2/6/5 | in 2nd floor | m2 | 5880 | 665 | 3910200
T2/6/6 | in 3rd floor | m2 | 3707 | 677 | 2509639
T2/6/7 | in 4th floor | m2 | 3082 | 690 | 2126580
T2/6/8 | in 5th floor | m2 | 3383 | 703 | 2378249
T2/6/9 | in 6th floor | m2 | 2154 | 716 | 1542264
T2/6/10 | in 7th floor | m2 | 2006 | 728 | 1460368
T2/6/11 | in 8th floor | m2 | 1937 | 741 | 1435317
Pump room, Machine Room
T2/6/12 | Pump room on water sump at lower ground floor level | m2 | 82 | 639 | 52398
T2/6/13 | Machine Room on roof slab | m2 | 161 | 756 | 121716
T2/6a | Finishing for concrete wall/ column (Isolated)
T2/6a | Finishing with AP kote wall putty/ joint compound- interior (one coat) on surfases of isolated RCC column, RCC wall, etc.
T2/6a/1 | From LG/F to 8th floor | m2 | 4800 | 691 | 3316800
T3 | Soffit finishing
T3/1 | Soffit finishing with AP kote wall putty/ joint compound- interior (one coat) on soffit of floor slabs, other slab, stair flight & beams
T3/1/1 | in L/G/ floor | m2 | 2002 | 189 | 378378
T3/1/2 | in Mezz. floor | m2 | 427 | 189 | 80703
T3/1/3 | in G/ floor | m2 | 560 | 189 | 105840
T3/1/4 | in 1st floor | m2 | 1718 | 193 | 331574
T3/1/5 | in 2nd floor | m2 | 1186 | 197 | 233642
T3/1/6 | in 3rd floor | m2 | 915 | 200 | 183000
T3/1/7 | in 4th floor | m2 | 741 | 204 | 151164
T3/1/8 | in 5th floor | m2 | 685 | 208 | 142480
T3/1/9 | in 6th floor | m2 | 506 | 212 | 107272
T3/1/10 | in 7th floor | m2 | 506 | 215 | 108790
T3/1/11 | in 8th floor | m2 | 284 | 219 | 62196
Pump room, Machine Room
T3/1/12 | Pump room on water sump at lower ground floor level | m2 | 71 | 189 | 13419
T3/1/13 | Machine Room on roof slab | m2 | 207 | 224 | 46368
T4 | Wall Tiling
T4/1 | 200mm x 400mm" ceramic glazed wall tiling on and including cement and sand screed backing and point with tile grout to match and forming neat uniform joints between tiles. Rate to include for forming edges and cutting tiles into required sizes and shape at corners, edges and where necessary and cleaning on completion. Price for 200x400mm tile shall be Rs 165.00 to 190.00)
up to the height of 1800mm. of toilet walls
T4/1/1 | in L/G/ floor | m2 | 302 | 3782 | 1142164
T4/1/2 | in Mezz. floor | m2 | 56 | 3782 | 211792
T4/1/3 | in G/ floor | m2 | 283 | 3782 | 1070306
T4/1/4 | in 1st floor | m2 | 520 | 3858 | 2006160
T4/1/5 | in 2nd floor | m2 | 498 | 3933 | 1958634
T4/1/6 | in 3rd floor | m2 | 780 | 4009 | 3127020
T4/1/7 | in 4th floor | m2 | 502 | 4085 | 2050670
T4/1/8 | in 5th floor | m2 | 390 | 4160 | 1622400
T4/1/9 | in 6th floor | m2 | 316 | 4236 | 1338576
T4/1/10 | in 7th floor | m2 | 339 | 4311 | 1461429
T4/1/11 | in 8th floor | m2 | 236 | 4387 | 1035332
T4/2 | - Ditto - but 1000x500 mm tile in rooms up to 1200mm hight. Price for 1000x500mm tile shall be Rs 1150.00 to 1200.00)
T4/2/1 | in G/ floor | m2 | 900 | 3935 | 3541500
T4/2/2 | in 1st floor | m2 | 1092 | 4014 | 4383288
T4/2/3 | in 2nd floor | m2 | 1439 | 4092 | 5888388
T4/2/4 | in 3rd floor | m2 | 270 | 4171 | 1126170
T4/2/5 | in 4th floor | m2 | 972 | 4250 | 4131000
T4/2/6 | in 5th floor | m2 | 853 | 4329 | 3692637
T4/2/7 | in 6th floor | m2 | 290 | 4407 | 1278030
T4/2/8 | in 7th floor | m2 | 290 | 4486 | 1300940
T4/2/9 | in 8th floor | m2 | 131 | 4565 | 598015
T4/3 | - Ditto - but 300x600 mm tile in rooms up to 1200mm hight. Price for 300x600mm tile shall be Rs 390.00 to 420.00)
T4/3/1 | in 8th floor | m2 | 131 | 4446 | 582426
T5 | External Plaster
T5/1 | Render 15mm thick cement and sand (1:5) and finish semi rough (Externally)
T5/1/1 | in L/G/ floor | m2 | 1509 | 397 | 599073
T5/1/2 | in Mezz. floor | m2 | 6 | 397 | 2382
T5/1/3 | in G/ floor | m2 | 1481 | 397 | 587957
T5/1/4 | in 1st floor | m2 | 1462 | 405 | 592110
T5/1/5 | in 2nd floor | m2 | 1472 | 413 | 607936
T5/1/6 | in 3rd floor | m2 | 1589 | 421 | 668969
T5/1/7 | in 4th floor | m2 | 1034 | 429 | 443586
T5/1/8 | in 5th floor | m2 | 1105 | 437 | 482885
T5/1/9 | in 6th floor | m2 | 1202 | 445 | 534890
T5/1/10 | in 7th floor | m2 | 646 | 453 | 292638
T5/1/11 | in 8th floor | m2 | 661 | 461 | 304721
Pump room, Machine Room
T5/1/12 | Pump room on water sump at lower ground floor level | m2 | 82 | 397 | 32554
T5/1/13 | Machine Room on roof slab | m2 | 155 | 471 | 73005
T6 | Skirting
T6/1 | 4" high skirting for 300mm x 600mm homogeneous polished porcelain floor tiles on cement and sand 1:3 bedding.
T6/1/1 | in L/G/ floor | m | 331 | 616 | 203896
T6/1/2 | in G/ floor | m | 106 | 616 | 65296
T6/1/3 | in 1st floor | m | 437 | 628 | 274436
T6/1/4 | in 2nd floor | m | 218 | 641 | 139738
T6/1/5 | in 3rd floor | m | 444 | 653 | 289932
T6/1/6 | in 4th floor | m | 733 | 665 | 487445
T6/1/7 | in 5th floor | m | 177 | 678 | 120006
T6/1/8 | in 6th floor | m | 160 | 690 | 110400
T6/1/9 | in 7th floor | m | 160 | 702 | 112320
T6/1/10 | in 8th floor | m | 219 | 715 | 156585
T6/2 | 100mm high skirting on 600mm x 600mm homogeneous mat finished porcelain floor tile in cement and sand 1:3 bedding.
T6/2/1 | in L/G/ floor | m | 950 | 551 | 523450
T6/2/2 | in G/ floor | m | 978 | 551 | 538878
T6/2/3 | in 1st floor | m | 977 | 562 | 549074
T6/2/4 | in 2nd floor | m | 799 | 573 | 457827
T6/2/5 | in 3rd floor | m | 716 | 584 | 418144
T6/2/6 | in 4th floor | m | 240 | 595 | 142800
T6/2/7 | in 5th floor | m | 560 | 606 | 339360
T6/2/8 | in 6th floor | m | 434 | 617 | 267778
T6/2/9 | in 7th floor | m | 434 | 628 | 272552
T6/2/10 | in 8th floor | m | 279 | 639 | 178281
T6/3 | 4" high skirting for Ordinary and smooth Cement rendering floor in cement and sand 1:3 bedding.
T6/3/1 | in L/G/ floor | m | 100 | 304 | 30400
T6/3/2 | in G/ floor | m | 20 | 304 | 6080
T6/3/3 | in 1st floor | m | 20 | 310 | 6200
T6/3/4 | in 2nd floor | m | 48 | 316 | 15168
T6/3/5 | in 3rd floor | m | 66 | 322 | 21252
T6/3/6 | in 4th floor | m | 39 | 328 | 12792
T6/3/7 | in 5th floor | m | 11 | 334 | 3674
T6/3/8 | in 6th floor | m | 21 | 340 | 7140
T6/3/9 | in 7th floor | m | 21 | 347 | 7287
T6/3/10 | in 8th floor | m | 21 | 353 | 7413
T7 | Ceiling Finishes
T7/1 | Supply and fixing 600mmx600mm suspended Gipsom board Flat ceiling, 6 mm thick ) including Al. frame frame work (hanging rod, T bars and any other accessories ). Rate shall include for expansion bolt, edge trim and provisions for services line, etc.
T7/1/1 | in L/G/ floor | m2 | 327 | 2592 | 847584
T7/1/2 | in G/ floor | m2 | 269 | 2592 | 697248
T7/1/3 | in 1st floor | m2 | 942 | 2644 | 2490648
T7/1/4 | in 2nd floor | m2 | 173 | 2696 | 466408
T7/1/5 | in 3rd floor | m2 | 419 | 2748 | 1151412
T7/1/5 | in 4th floor | m2 | 586 | 2800 | 1640800
T7/1/6 | in 5th floor | m2 | 360 | 2852 | 1026720
T7/1/7 | in 6th floor | m2 | 227 | 2903 | 658981
T7/1/8 | in 7th floor | m2 | 232 | 2955 | 685560
T7/1/9 | in 8th floor | m2 | 316 | 3007 | 950212
T7/2 | - Ditto- but finished with concealed panel
T7/2/1 | in L/G/ floor | m2 | 735 | 4545 | 3340575
T7/2/2 | in G/ floor | m2 | 343 | 4545 | 1558935
T7/3 | Supply and fixing suspended Metal ceiling system (600mmx600mm) as per manufactures specification ("Chicago Metallic" or equivalent) to engineers approval. Rate shall include for expansion bolt, edge trim, any other accessories and provisions for services line, etc.
T7/3/1 | in L/G/ floor | m2 | 190 | 5114 | 971660
T7/3/2 | in G/ floor | m2 | 2070 | 5114 | 10585980
T7/3/3 | in 1st floor | m2 | 990 | 5217 | 5164830
T7/3/4 | in 2nd floor | m2 | 1571 | 5319 | 8356149
T7/3/5 | in 3rd floor | m2 | 603 | 5421 | 3268863
T7/3/6 | in 4th floor | m2 | 356 | 5523 | 1966188
T7/3/7 | in 5th floor | m2 | 1157 | 5626 | 6509282
T7/3/8 | in 6th floor | m2 | 330 | 5728 | 1890240
T7/3/9 | in 7th floor | m2 | 330 | 5830 | 1923900
T7/3/10 | in 8th floor | m2 | 378 | 5933 | 2242674
T7/4 | - Ditto- but Metal ceiling, with Antibacterial coating
T7/4/1 | in L/G/ floor | m2 | 36 | 5366 | 193176
T7/4/2 | in G/ floor | m2 | 305 | 5366 | 1636630
T7/4/3 | in 1st floor | m2 | 202 | 5474 | 1105748
T7/4/4 | in 2nd floor | m2 | 155 | 5581 | 865055
T7/4/5 | in 5th floor | m2 | 134 | 5903 | 791002
| TOTAL CARRIED TO SUMMARY |  |  | Rs. | 267292814.846

## Painting
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
BILL OF QUANTITIES |  | PAINTING
ITEM NO | DESCRIPTION | UNIT | QTY. | RATE (RS) | AMOUNT (RS)
V/- | PAINTING
V/1 | Prepare & apply one under coat & two finishing coats of weather shield paint to external plaster surface of walls & columns in following floors including preparing surface.
V/1/1 | in Lower ground floor | m2 | 1509 | 410 | 618690
V/1/2 | in Mezzanine floor | m2 | 6 | 410 | 2460
V/1/3 | in ground floor | m2 | 1481 | 410 | 607210
V/1/4 | in first floor | m2 | 1462 | 418 | 611116
V/1/5 | in 2 nd floor | m2 | 1472 | 426 | 627072
V/1/6 | in 3 rd floor | m2 | 1589 | 435 | 691215
V/1/7 | in 4 th floor | m2 | 1034 | 443 | 458062
V/1/8 | in 5 th floor | m2 | 1105 | 451 | 498355
V/1/9 | in 6 th floor | m2 | 1202 | 459 | 551718
V/1/10 | in 7 th floor | m2 | 646 | 467 | 301682
V/1/11 | in 8th floor | m2 | 661 | 476 | 314636
V/1/12 | Above 8th floor | m2 | 237 | 484 | 114708
V/2 | Finish with single coat of putty and prepare & apply one under coat & two finishing coats of Emulsion paint to internal plaster surface of walls in following floors, including preparing surface.
V/2/1 | in Lower ground floor | m2 | 8577 | 518 | 4442886
V/2/2 | in Mezzanine floor | m2 | 346 | 518 | 179228
V/2/3 | in ground floor | m2 | 8114 | 518 | 4203052
V/2/4 | in first floor | m2 | 4750 | 528 | 2508000
V/2/5 | in 2 nd floor | m2 | 5880 | 539 | 3169320
V/2/6 | in 3 rd floor | m2 | 3707 | 549 | 2035143
V/2/7 | in 4 th floor | m2 | 3082 | 559 | 1722838
V/2/8 | in 5 th floor | m2 | 3383 | 570 | 1928310
V/2/9 | in 6 th floor | m2 | 2154 | 580 | 1249320
V/2/10 | in 7 th floor | m2 | 2006 | 591 | 1185546
V/2/11 | in 8th floor | m2 | 1937 | 601 | 1164137
V/2/12 | Above 8th floor | m2 | 243 | 611 | 148473
V/3 | Prepare & apply one under coat & two finishing coats of Emulsion paint to skim coated surface of soffits in following floors, including preparing surface.
V/3/1 | in Lower ground floor | m2 | 2002 | 382 | 764764
V/3/2 | in Pump room on water sump at lower ground floor level | m2 | 71 | 382 | 27122
V/3/3 | in Mezzanine floor | m2 | 427 | 382 | 163114
V/3/4 | in ground floor | m2 | 560 | 382 | 213920
V/3/5 | in first floor | m2 | 1718 | 390 | 670020
V/3/6 | in 2 nd floor | m2 | 1186 | 397 | 470842
V/3/7 | in 3 rd floor | m2 | 915 | 405 | 370575
V/3/8 | in 4 th floor | m2 | 741 | 413 | 306033
V/3/9 | in 5 th floor | m2 | 685 | 420 | 287700
V/3/10 | Above 8th floor - Machine Room on roof slab | m2 | 207 | 451 | 93357 | 8512
V/4 | Finish with single coat of putty and prepare & apply one under coat & two finishing coats of emulsion paint to surface of Ceiling in following floors, including preparing surface.
V/4/1 | in Lower ground floor | m2 | 327 | 571 | 186717
V/4/2 | in G/ floor | m2 | 269 | 571 | 153599
V/4/3 | in 1st floor | m2 | 942 | 582 | 548244
V/4/4 | in 2nd floor | m2 | 173 | 594 | 102762
V/4/5 | in 3rd floor | m2 | 419 | 605 | 253495
V/4/6 | in 5th floor | m2 | 360 | 628 | 226080
V/4/7 | in 6th floor | m2 | 227 | 640 | 145280
V/4/8 | in 7th floor | m2 | 232 | 651 | 151032
V/4/9 | in 8th floor | m2 | 316 | 662 | 209192 | 3265
| TOTAL CARRIED TO SUMMARY. |  |  | Rs. | 34677025

## miscell
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
BILL OF QUANTITIES |  | MISCELLANEOUS
ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT (RS)
Y- MISCELLANEOUS
Y/1 | RCC beam, 112.5x100mm on brick wall at stair way and balcony. Rate shall include for 2 / 10mm dia tor steel bar, 6mm link at 250 c/c and form work for concrete | m | 273 | 1169 | 319137
Y/2 | RCC Coping, 150mm wide x height varies 100 ~75 mm on RCC upstand wall (measured seperetly) at terros. Rate shall include for 2 / 10mm dia tor steel bar, 6mm link at 250 c/c form work for concrete
Y/2/1 | In single story building at Lower G/F | m | 91 | 1296 | 117936 |  |  | 0
Y/2/2 | In 1st floor slab level | m | 70 | 1322 | 92540 | Addendum01
Y/2/3 | In 2nd floor slab level | m | 154 | 1348 | 207592 | Addendum01
Y/2/4 | In 3rd floor slab level | m | 98 | 1374 | 134652 | Addendum01 | 3
Y/2/5 | In 6th floor slab level | m | 210 | 1452 | 304920 | Addendum01
Y/2/6 | In roof slab level | m | 133 | 1529 | 203357 | Addendum01
Y/3 | RCC Lintal, 112.5x100mm on 112.5 thick brick wall over the window/ door etc at lower G/ floor to 8th floor. Rate shall include for 2 / 10mm dia tor steel bar, 6mm link at 250 c/c and form work for concrete | m | 575 | 1355 | 779125
Y/3/1 | - dito- but 112.5x150mm | m | 200 | 1513 | 302600
Y/3/2 | - dito- but 112.5x300mm | m | 200 | 2839 | 567800
Y/4 | RCC Lintal, 225x150mm on 225 thick brick wall over the window/ door etc at lower G/ floor to 8th floor. Rate shall include for 4 / 10mm dia tor steel bar, 6mm stirup at 100 c/c and form work for concrete | m | 780 | 2747 | 2142660
Y/5 | - dito- but 225x225mm and 4/12mm dia bar and 6mm stirup at 150 c/c | m | 115 | 3948 | 454020
Y/6 | - dito- but 225x300mm and 4/16mm dia bar and 6mm stirup at 100 c/c | m | 115 | 5554 | 638710
Y/7 | - dito- but 225x450mm and 5/16mm dia bar and 10mm stirup at 175 c/c | m | 80 | 8151 | 652080
Y/7a | RCC Vanity top, 600x75mm on 112.5 thick brick wall at lower G/ floor to 8th floor. Rate shall include for 10mm dia tor steel bar, 250 c/c, both way and form work for concrete | m | 158 | 7711 | 1218338
Y/8 | Water sump @ Lower ground floor
Refer Dwg No: HB/ST/24
Y/8/1 | Providing 3mm thk. Chequered plate Manhole cover to opening of top slab (800x800mm). Rate shall include for 2 nos. of hinges and locking arrangement (pad lock) | Item | 1 | 8142 | 8142
Y/8/2 | Providing step rungs embedded to RCC wall below the opening, in 25mm dia heavy duty G.I. pipes including painting | Nr | 10 | 1170 | 11700
Y/8/3 | Providing water stop bar, 10mm thick, 400mm wide MS plate along wall | m | 56 | 6298 | 352688
Y/9 | Over head water tank, 5.5x14x2 m
Y/9/1 | Providing 3mm thk. Chequered plate Manhole cover to opening of top slab (800x800mm). Rate shall include for 2 nos. of hinges and locking arrangement (pad lock) | Item | 1 | 8142 | 8142
Y/9/2 | Providing step rungs embedded to RCC wall (inside & out side of tank) below the opening , in 25mm dia heavy duty G.I. pipes including painting | Nr. | 8 | 1170 | 9360
Y/9/3 | Providing water stop bar, 10mm thick, 400mm wide MS plate along wall | m | 38 | 6298 | 239324
Y/9/4 | Providing Upvc inlet pipe (75mm dia, type 1000), outlet pipe, overflow pipe and washout pipe, | Item | 1 | 4705 | 4705
Y/10 | Wall, Doors and Door frames Protection
Supply and embedded trolley guard in to walls along passages etc. as per manufactures specification ("Acrovyn"or equivalent) to engineers approval . Rate shall include for expansion joint, edge trim, and any other accessories to completion
Y/10/1 | to walls, 225mm wide x 20mm, curved
Y/10/1/1 | at Lower G/F | m | 417 | 1521 | 634257
Y/10/1/2 | at G/F | m | 430 | 1521 | 654030
Y/10/1/3 | at 1st Floor | m | 340 | 1551 | 527340
Y/10/1/4 | at 2nd Floor | m | 410 | 1582 | 648620
Y/10/1/5 | at 3rd Floor | m | 300 | 1612 | 483600
Y/10/1/6 | at 4th Floor | m | 360 | 1643 | 591480
Y/10/1/7 | at 5th Floor | m | 275 | 1673 | 460075
Y/10/1/8 | at 6th Floor | m | 180 | 1704 | 306720
Y/10/1/9 | at 7th Floor | m | 180 | 1734 | 312120
Y/10/1/10 | at 8th Floor | m | 200 | 1764 | 352800
Y/10/2 | to corners at columns and wall joints, 100 x 100 x 20 mm, 1.0m hight L
Y/10/2/1 | at Lower G/F | set | 12 | 919 | 11028
Y/10/2/2 | at G/F | set | 68 | 919 | 62492
Y/10/2/3 | at 1st Floor | set | 44 | 937 | 41228
Y/10/2/4 | at 2nd Floor (Provisional Qty) | set | 1 | 956 | 956
Y/10/2/5 | at 3rd Floor | set | 1 | 974 | 974
Y/10/2/6 | at 4th Floor | set | 1 | 993 | 993
Y/10/2/7 | at 5th Floor | set | 1 | 1011 | 1011
Y/10/2/8 | at 6th Floor | set | 1 | 1029 | 1029
Y/10/2/9 | at 7th Floor | set | 1 | 1048 | 1048
Y/10/2/10 | at 8th Floor | set | 1 | 1066 | 1066
Y/10/3 | to doors , 150 x 600 mm x 20mm
Y/10/3/1 | at Lower G/F | set | 20 | 606 | 12120
Y/10/3/2 | at G/F | set | 50 | 606 | 30300
Y/10/3/3 | at 1st Floor | set | 20 | 618 | 12360
Y/10/3/4 | at 2nd Floor | set | 40 | 630 | 25200
Y/10/3/5 | at 3rd Floor | set | 35 | 642 | 22470
Y/10/3/6 | at 4th Floor | set | 35 | 654 | 22890
Y/10/3/7 | at 5th Floor | set | 30 | 667 | 20010
Y/10/3/8 | at 6th Floor | set | 14 | 679 | 9506
Y/10/3/9 | at 7th Floor | set | 14 | 691 | 9674
Y/10/3/10 | at 8th Floor | set | 23 | 703 | 16169
Y/11 | Interlocking Paving
Y/11/1 | Furnish and lay Interlocking blocks (9x3.5x4 inch) on 75mm thick sand/ qarry dust layer.
Y/11/1/1 | in Lower G/F (Kitchen yard) | m2 | 110 | 3197 | 351670
Y/11/1/2 | in G/F (Court yard) | m2 | 98 | 3197 | 313306
Y/12 | Perporated pipe
Y/12/1 | Furnish and lay U.pvc Perorated pipe, type 600, 110mm dia as per Dwg. No: HB/ST/08/T. Rate shall include for necessary excavation, aggregate filling, filter cloth and back filling etc.
Y/12/1/1 | at G/F level | m | 118 | 6392 | 754256
| PROVISIONAL SUMS CARRIED TO SUMMARY |  |  | Rs. | 15462326

## Money provision
PROPOSED DISTRICT GENERAL HOSPITAL AT HAMBANTOTA
CONSTRUCTION AND COMPLETION OF MAIN BUILDING (BLOCK-E)
BILL OF QUANTITIES |  | MONEY PROVISION
ITEM NO | DESCRIPTION | UNIT | QTY | AMOUNT (RS) (Nominated Sub Contractor) | AMOUNT (RS) Main Contractor
Z- MONEY PROVISION - NOMINATED SUB CONTRACTS WORK (NSCW)
Following Provisional sums shall be used by as directed by the Employer/ Consultant and deduct in whole or part if not ordered to be used.
Whole or part of the items shall be awarded to a nominated sub contractor.
Main Contractor shall facilitate to complete NSCW (Providing Stores facility, electricity, water, etc. and keeping proper cordination when NSCW conjunction with civil works)
Nominated Sub Contractor's Payments shall be made directly to him
Main contractor shall undertake the relevant builder's work related to NSCW, and shall be paid based on relevent rates available in the contract.
Main Contractor shall be entitled to an attendance fee, as a percentage of value of NSCW, (quoted below).
Nominated Sub Contractor shall provide shop drawings, warranties as required, handing over notes and commissioning
Z/01 | Provisional sum for Providing Water supply , Soil and waste water System (internal & external) and supply and fixing of Sanitary fittings . | Item | P.Sum | 50000000
Z/01a | Main Contractor's Attendence fee related to above NSCW (10%) | Item |  |  | 5000000
Z/01b | Provisional sum for builder's work (to be done by main contractor) related to above NSCW. | Item | P.Sum |  | 3500000
Z/02 | Provisional sum for providing Mechanical Installation (Elevators) | Item | P.Sum | 24000000
Z/02a | Main Contractor's Attendence fee related to above NSCW (5%) | Item |  |  | 1200000
Z/02b | Provisional sum for builder's work (to be done by main contractor) related to above NSCW. | Item | P.Sum |  | 1680000
Z/03 | Provisional sum for providing Mechanical Installation (Fire Protection system) | Item | P.Sum | 18000000
Z/03a | Main Contractor's Attendence fee related to above NSCW (8%) | Item |  |  | 1440000
Z/03b | Provisional sum for builder's work (to be done by main contractor) related to above NSCW. | Item | P.Sum |  | 1260000
Z/04 | Provisional sum for providing Mechanical Installation (Medical gas system ) | Item | P.Sum | 15000000
Z/04a | Main Contractor's Attendence fee related to above NSCW (8%) | Item |  |  | 1200000
Z/04b | Provisional sum for builder's work (to be done by main contractor) related to above NSCW. | Item | P.Sum |  | 1050000
Z/05 | Provisional sum for providing Mechanical Installation (Air conditioning) | Item | P.Sum | 75000000
Z/05a | Main Contractor's Attendence fee related to above NSCW (10%) | Item |  |  | 7500000
Z/05b | Provisional sum for builder's work (to be done by main contractor) related to above NSCW. | Item | P.Sum |  | 5250000
Z/06 | Provisional sum for providing Sewage treatment plant | Item | P.Sum | 29000000
Z/06a | Main Contractor's Attendence fee related to above NSCW (5%) | Item |  |  | 1450000
Z/06b | Provisional sum for builder's work (to be done by main contractor) related to above NSCW. | Item | P.Sum |  | 2030000
| PROVISIONAL SUMS CARRIED TO SUMMARY |  |  | 211000000 | 14770000
17790000
32560000
211000000